| CATHODIC PROTECTION — GALVANIC WEST VIRGINIA UNDERGROUND STORAGE TANKS |
| --- |
|  | WV Department of Environmental Protection Division of Water and Waste Management Environmental Enforcement/ UST Unit http://www.dep.wv.gov/WWE/ee/ust/Pages/default.aspx | 601 57th Street, S.E. Charleston, WV 25304 Phone (304) 926-0470 Fax (304) 926-0457 | REV. 3/23/2010 |
| This form must be utilized to evaluate underground storage tank (UST) galvanic cathodic protection (CP) systems in the State of West Virginia. A copy of this completed form must be submitted by the owner /operator to the WVDEP UST Section within 30 days of testing. A site drawing depicting the UST cathodic protection system and all reference electrode placements must be completed. |
| I. UST OWNER: |  | II. UST FACILITY |
| Contact Name: | Phone: | Name: | Facility ID: |
| Address: | Address: |
| City: | State: | City: | County: |
| III. REASON SURVEY WAS CONDUCTED (mark only one) | Routine – 3 year Routine – within 6 months of installation/upgrade/modification Re-survey upon achievement of steady-state polarization immediately following upgrade/modification (complete Section IX) |
| IV. CATHODIC PROTECTION TESTER’S EVALUATION (mark only one) |
| PASS FAIL INCONCLUSIVE | All protected structures at this facility pass the cathodic protection and continuity survey (indicate all criteria applicable by completion of Section V). No further action is necessary at this time. Next test is due in 3 years. One or more protected structures at this facility fail the cathodic protection and/or continuity survey. Refer to a corrosion expert for further evaluation OR permanently close. If the remote and the local do not both indicate the same test result on all protected structures (both pass or both fail), inconclusive is indicated and/or if the continuity survey indicates inconclusive or continuous results, a corrosion expert must evaluate the survey and complete Section VI. |
| Tester Name: | WVDEP Certification Number: |
| Company Name: | Certifying Organization & Number (e.g., NACE): |
| Address: | Certification Type (e.g., CP Tester, CP Technician): |
| City: | State: | Zip: | Phone: |
| CP Tester’s Signature: | Date Signed: | Date CP Survey Performed: |
| V. CRITERIA APPLICABLE TO TESTER’S EVALUATION (mark all that apply) |
| 850 mV ON 850 mV Instant OFF 100 mV Polarization | Structure-to-soil potential more negative than -850 mV with respect to a Cu/CuSO4 reference electrode with protective current applied (This criterion is applicable to any galvanic protected structure). Structure-to-soil potential more negative than -850 mV with respect to a Cu/CuSO4 reference electrode with protective current temporarily interrupted (This criterion is applicable only to those galvanic systems where the anodes can be disconnected). Structure tested exhibits at least 100 mV of cathodic polarization. (This criterion is applicable only to those galvanic systems where the anodes can be disconnected). |
| VI. CORROSION EXPERT’S EVALUATION IF REQUIRED (mark only one) |
| The survey must be conducted and/or evaluated by a corrosion expert when: a) an inconclusive is indicated for any protected structure since both the local and the remote structure-to-soil potentials do not result in the same outcome; b) upgrades to steel piping protected by galvanic systems are conducted; c) supplemental anodes are added to the tanks and/or piping without following an accepted industry code; or d) when required by WVDEP. |
| PASS FAIL | All protected structures at this facility are judged to have adequate cathodic protection and therefore pass the CP and continuity survey. Indicate all criteria applicable: -850 mV ON -850 mV Instant OFF 100 mV Polarization One or more tested structures at this facility do not pass the CP and/or continuity survey and it is judged that adequate CP is not currently being provided to the UST system (indicate what action is necessary by completion of Section VII). |
| Corrosion Expert’s Name: | WVDEP Class D Cert. #: | NACE Int’l Cert. Type / Professional Engineer (PE) Specialty: |
| Company Name: | NACE Int’l Cert. Number or RPE Number / State: |
| Address: | City: | State: | Zip: | Phone: |
| Corrosion Expert’s Signature: | Date: |
| VII. ACTION REQUIRED AS A RESULT OF EXPERT’S EVALUATION (mark only one) |
| NONE UPGRADE & RETEST | Cathodic protection (CP) is adequate. No further action is necessary at this time. Cathodic protection is not adequate. Immediately upgrade per industry standard or corrosion expert design OR permanently close. If upgraded, system must be retested within 6 months after the upgrade. |
| Next cathodic protection survey due | (required every 3 years and within 6 months of upgrades) |
| WV Department of Environmental Protection 601 57th Street, S.E. Division of Water and Waste Management Charleston, WV 25304 Environmental Enforcement/ UST Unit (304) 926-0470 |
| CATHODIC PROTECTION — GALVANIC | Pg. 2 of 5 |
| VIII. DESCRIPTION OF UST SYSTEM |
| TANK # | PRODUCT STORED (PREMIUM, DIESEL, ETC.) | TANK CAPACITY (GAL) | CONSTRUCTION MATERIAL | FLEX CONNECTORS (Bonded, isolated, booted, anode, N/A) |
|  |  |  | TANKS | PIPING | SIPHON LINE |  |
| 1 |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |
| IX. DESCRIPTION OF CATHODIC PROTECTION SYSTEM UPGRADES AND/OR MODIFICATIONS |
| Cathodic protection systems must be evaluated within 6 months after any upgrades and/or modifications. Complete this section if any upgrades or modifications were made to the cathodic protection system in response to a “failed” evaluation. Certain upgrades/modifications as determined by WVDEP are required to be designed and/or evaluated by a corrosion expert (completion of Section VI required). |
| Supplemental anodes for a Sti-P3 tank were added (attach corrosion expert’s design or document industry standard used). Supplemental anodes for metallic pipe or flex-connectors were added (attach corrosion expert’s design or document industry standard used). Galvanically protected tanks/piping not electrically isolated (explain upgrades/modifications completed in “Remarks/Other” below). |
| Remarks/Other: |
| WV Department of Environmental Protection 601 57th Street, S.E. Division of Water and Waste Management Charleston, WV 25304 Environmental Enforcement/ UST Unit (304) 926-0470 |
| CATHODIC PROTECTION — GALVANIC | 3 of 5 |
| X. UST FACILITY SITE DRAWING |
| Attach detailed drawing of the UST and cathodic protection systems. Sufficient detail must be given in order to clearly indicate where the reference electrode was placed for each structure-to-soil potential that is recorded on the survey forms. Any pertinent data must also be included. At a minimum you should indicate the following: All tanks, piping and dispensers; All buildings and streets; All anodes and wires; Location of CP test stations; Each reference electrode placement must be indicated by a code (e.g., 1,2,3… T-1, T-2, P-1, P-2… etc.), corresponding with the appropriate line number in Section XII of this form. |
| AN EVALUATION OF THE CATHODIC PROTECTION SYSTEM IS NOT COMPLETE WITHOUT AN ACCEPTABLE SITE DRAWING. |
| WV Department of Environmental Protection 601 57th Street, S.E. Division of Water and Waste Management Charleston, WV 25304 Environmental Enforcement/ UST Unit (304) 926-0470 |

| CATHODIC PROTECTION — GALVANIC | Pg. 4 of 5 |
| --- | --- |
| XI. GALVANIC (SACRIFICIAL ANODE) CATHODIC PROTECTION SYSTEM CONTINUITY SURVEY |
| This section may be utilized to document measurements of continuity on underground storage tank systems that are protected by CP systems. When conducting a fixed cell – moving ground survey, the reference electrode must be placed in the soil at a remote location and left undisturbed. Conduct point-to-point test between any two structures for which the fixed cell-moving ground survey is inconclusive or indicates possible continuity. For galvanic systems, the structure that is to be protected must be isolated from any other metallic structure in order to pass the continuity survey. |
| FACILITY NAME: |  | NOTE: The survey is not complete unless all other applicable parts of this form are also completed |
| DESCRIBE LOCATION OF “FIXED REMOTE” REFERENCE ELECTRODE PLACEMENT: |  |
| STRUCTURE “A” 1 | STRUCTURE “B” 2 | STRUCTURE “A” 3 FIXED REMOTE VOLTAGE | STRUCTURE “B” 4 FIXED REMOTE VOLTAGE | POINT-TO-POINT 5 VOLTAGE DIFFERENCE | ISOLATED/ 6 CONTINUOUS/ INCONCLUSIVE |
| (example) PREMIUM TANK BOTTOM | (example) PREMIUM TANK FILL RISER | (example) -921 mV | (example) -915 mV |  | (example) INCONCLUSIVE |
| (example) PREMIUM TANK BOTTOM | (example) PREMIUM TANK FILL RISER |  |  | (example) 17 mV | (example) ISOLATED |
| COMMENTS: |
| 1) Describe the cathodically protected structure {“A”} that you are trying to show is isolated from unprotected structures (e.g., premium tank). 2) Describe the unprotected structure {“B”} that you are attempting to demonstrate is isolated from the protected structure (e.g., Premium tank fill riser). 3) Record the measured structure-to-soil potential of the protected structure {“A”} in millivolts (e.g., -921 mV). 4) Record the measured structure-to-soil potential of the unprotected structure {“B”} in millivolts (e.g., -915 mV). 5) Record the voltage observed between structure “A” and structure “B” when conducting “point-to-point” testing (e.g., 17 mV). 6) Document whether the test indicated the protected structure was isolated, continuous or inconclusive, according to the chart below. |
| Isolated Voltage difference is >10 mV | Continuous Voltage difference is ≤1 mV | Inconclusive Voltage difference is > 1 mV but ≤10 mV |
| WV Department of Environmental Protection 601 57th Street, S.E. Division of Water and Waste Management Charleston, WV 25304 Environmental Enforcement/ UST Unit (304) 926-0470 |
| CATHODIC PROTECTION — GALVANIC | Pg. 5 of 5 |
| XII. CATHODIC PROTECTION SYSTEM SURVEY |
| This section must be used to document a survey of a galvanic system by obtaining structure-to-soil potential measurements. At a minimum the reference electrode must be placed in the soil at both ends and the middle centerline of each tank and both ends of each piping run. STIP3 tank alternative: In lieu of the above method, a reading may be taken over the center of the tank midline and 1 remote reading at least 30’ away from the structure being tested. Both the local and the remote voltage must be -850 mV or more negative in order to pass. Inconclusive is indicated when both the local & remote structure-to-soil potentials do not result in the same outcome (Both must pass or both fail) If the 100 mV polarization method is used to verify adequate CP on a system for which anodes can be disconnected, please use page 5 of the CATHODIC PROTECTION IMPRESSED CURRENT form. |
| FACILITY NAME: |  | NOTE: The survey is not complete unless all other applicable parts of this form are also completed |
| DESCRIBE LOCATION OF REMOTE REFERENCE ELECTRODE PLACEMENT: |  |
| LOCATION CODE1 | STRUCTURE 2 | CONTACT POINT 3 | REFERENCE CELL PLACEMENT 4 | LOCAL VOLTAGE5 | Remote VOLTAGE6 | PASS / FAIL /INCONCLUSIVE7 |
| (example) T-2 | (example) PREM TANK | (example) TANK BOTTOM | (example) SOIL @ PREM TANK STP MANWAY | (example) -928 mV | (example) -810 mV | (example) INCONC. |
| (example) P-1 | (example) PLUS PIPING | (example) DISPENSER 5/6 | (example) SOIL UNDER DISPENSER 5/6 | (example) -890 mV | (example) -885 mV | (example) PASS |
| COMMENTS: |
| 1) Designate numerically or by code on the site drawing each “local” reference electrode placement (e.g., 1,2,3… T-1, T-2, P-1, P-2…etc.). 2) Describe the structure that is being tested (e.g., plus tank; premium piping; diesel submersible pump flex connector; etc.). 3) Describe where contact with the structure being tested is made (e.g., T1 test lead, plus tank bottom; diesel piping @ dispenser 7/8;PP4, etc.). 4) Describe the exact location where reference electrode is placed for each measurement (e.g., soil @ regular tank STP manway; soil @ dispenser 2, etc.). 5) Record the structure-to-soil potential measured with the reference electrode placed “local” in millivolts (e.g., -865 mV, -920 mV, etc.). 6) Record the structure-to-soil potential measured with the reference electrode placed “remote” (copy voltage that was obtained during continuity survey). 7) Indicate if the tested structure passed or failed the -850 mV “on” criterion based on your interpretation of data. |