| CATHODIC PROTECTION — IMPRESSED CURRENT WEST VIRGINIA UNDERGROUND STORAGE TANKS |
| --- |
|  | WV Department of Environmental Protection Division of Water and Waste Management Environmental Enforcement/ UST Unit http://www.dep.wv.gov/WWE/ee/ust/Pages/default.aspx | 601 57th Street, S.E. Charleston, WV 25304 P (304) 926-0470 F (304) 926-0457 | REV. 3/23/2010 |
| This form must be utilized to evaluate underground storage tank (UST) impressed current cathodic protection systems in the State of West Virginia. A copy of this completed form must be kept available & submitted by the owner /operator to the WVDEP UST Section upon request. A site drawing depicting the UST cathodic protection system and all reference electrode placements must be completed. |
| I. UST OWNER: |  | II. UST FACILITY |
| Contact Name: | Phone: | Name: | Facility ID: |
| Address: | Address: |
| City: | State: | City: | County: |
| III. REASON SURVEY WAS CONDUCTED (mark only one) | Routine – 3 year Routine – within 6 months of installation /upgrade/modification Re-survey upon achievement of steady-state polarization immediately following upgrade/modification (complete Section XI) |
| IV. CATHODIC PROTECTION TESTER’S EVALUATION (mark only one) |
| PASS FAIL INCONCLUSIVE | All protected structures at this facility pass the cathodic protection and continuity survey (indicate all criteria applicable by completion of Section V). No further action is necessary at this time. Next test is due in 3 years. One or more protected structures at this facility fail the cathodic protection and/or continuity survey. Refer to a corrosion expert for further evaluation OR permanently close. If any potential does not meet criteria or if any structure is discontinuous, a corrosion expert must evaluate the survey and complete Section VI. |
| Tester Name: | WV DEP Certification Number: |
| Company Name: | Certifying Organization & number(e.g., NACE): |
| Address: | Certification Type (e.g., CP Tester, CP Technician): |
| City: | State: | Zip: | Phone: |
| CP Tester’s Signature: | Date Signed: | Date CP Survey Performed: |
| V. CRITERIA APPLICABLE TO TESTER’S EVALUATION (mark all that apply) |
| 850 mV Instant OFF 100 mV Polarization | Structure-to-soil potential more negative than -850 mV with respect to a Cu/CuSO4 reference electrode with protective current temporarily interrupted (instant-off). Structure tested exhibits at least 100 mV of cathodic polarization. |
| VI. CORROSION EXPERT’S EVALUATION IF REQUIRED (mark only one) |
| The survey must be evaluated by a corrosion expert when: a) supplemental anodes or other changes in the construction of the impressed current system are made; b) a stray current may be affecting buried metallic structures; c) an inconclusive result was indicated in Section IV; or d) when required by WVDEP. |
| PASS FAIL | All protected structures at this facility are judged to have adequate cathodic protection and therefore pass the cathodic protection and continuity survey. Indicate all criteria applicable: -850 mV Instant OFF 100 mV Polarization One or more protected structures at this facility do not pass the cathodic protection and/or continuity survey and it is judged that adequate cathodic protection is not currently being provided to the UST system (indicate what action is necessary by completion of Section VII). |
| Corrosion Expert’s Name: | WVDEP Class D Cert. #: | NACE Int’l Cert. Type / Professional Engineer (PE) Specialty: |
| Company Name: | NACE Int’l Cert. Number or RPE Number / State: |
| Address: | City: | State: | Zip: | Phone: |
| Corrosion Expert’s Signature: | Date: |
| VII. ACTION REQUIRED AS A RESULT OF CORROSION EXPERT EVALUATION (mark only one) |
| NONE UPGRADE & RETEST | Cathodic protection is adequate. No further action is necessary at this time. Cathodic protection is not adequate. Immediately upgrade per industry standard or corrosion expert design OR permanently close. If upgraded, system must be retested within 6 months after the upgrade. |
| Date next cathodic protection survey due |  | (required every 3 years and within 6 months of upgrades) |
| WV Department of Environmental Protection Division of Water and Waste Management Environmental Enforcement/ UST Unit http://www.dep.wv.gov/WWE/ee/ust/Pages/default.aspx 601 57th Street, S.E. Charleston, WV 25304 P (304) 926-0470 F (304) 926-0457 |
| CATHODIC PROTECTION — IMPRESSED CURRENT | Pg. 2 of 7 |
| VIII. DESCRIPTION OF UST SYSTEM |
| TANK # | PRODUCT STORED (PREMIUM, DIESEL, ETC.) | TANK CAPACITY (GAL) | CONSTRUCTION MATERIAL | FLEX CONNECTORS (Bonded, isolated, booted, anode, N/A) |
|  |  |  | TANKS | PIPING | SIPHON LINE |  |
| 1 |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |
| IX. IMPRESSED CURRENT RECTIFIER DATA (complete all that are applicable) |
| Rectifier Manufacturer: | Note: In order to conduct an effective evaluation of the cathodic protection system, a complete evaluation of the rectifier is necessary. |
| Rectifier Model: | Rectifier Serial Number: |
| Previous Rectifier Output as Left at Last Test |  | Volts |  | Amps | Rated DC Output: |  | Volts |  | Amps |
| EVENT | DATE | TAP SETTINGS | DC OUTPUT | HOUR METER | COMMENTS |
|  |  | COARSE | FINE | VOLTS | AMPS |  |  |
| “AS FOUND” |  |  |  |  |  |  |  |
| “AS LEFT” |  |  |  |  |  |  |  |
| X. IMPRESSED CURRENT POSITIVE & NEGATIVE CIRCUIT MEASUREMENTS (output amperage) |
| Complete if the system is designed to allow such measurements (i.e. individual lead wires for each anode are installed and measurement shunts are present). |
| CIRCUIT |  |  |  |  |  |  |  |  |  |  | TOTAL |
| ANODE (+) |  |  |  |  |  |  |  |  |  |  |  |
| TANK (-) |  |  |  |  |  |  |  |  |  |  |  |
| XI. DESCRIPTION OF CATHODIC PROTECTION SYSTEM UPGRADES AND/OR MODIFICATIONS |
| Cathodic protection systems must be evaluated within 6 months after any upgrades and/or modifications. Complete this section if any upgrades or modifications were made to the cathodic protection system in response to a “failed” evaluation. Certain upgrades/modifications as determined by WVDEP are required to be designed and/or evaluated by a corrosion expert (completion of Section VI required). |
| Supplemental anodes for an impressed current system were needed (attach corrosion expert’s design). Repairs or replacement of rectifier was needed (explain in “Remarks/Other” below). Repair or replacement of anode header cables were needed (explain in “Remarks/Other” below). Impressed current tanks/piping are not electrically continuous (explain upgrades/modifications completed in “Remarks/Other” below). Adjustments were made to the rectifier output. |
| Remarks/Other: |
| WV Department of Environmental Protection Division of Water and Waste Management Environmental Enforcement/ UST Unit http://www.dep.wv.gov/WWE/ee/ust/Pages/default.aspx 601 57th Street, S.E. Charleston, WV 25304 P (304) 926-0470 F (304) 926-0457 |
| CATHODIC PROTECTION — IMPRESSED CURRENT | 3 of 7 |
| XII. UST FACILITY SITE DRAWING |
| Attach detailed drawing of the UST and cathodic protection systems. Sufficient detail must be given in order to clearly indicate where the reference electrode was placed for each structure-to-soil potential that is recorded on the survey forms. Any pertinent data must also be included. At a minimum you should indicate the following: All tanks, piping and dispensers; All buildings and streets; All anodes and wires; Location of CP test stations; Each reference electrode placement must be indicated by a code (e.g., 1,2,3… T-1, T-2, P-1, P-2… etc.) corresponding with the appropriate line number in Section XIV of this form. |
| AN EVALUATION OF THE CATHODIC PROTECTION SYSTEM IS NOT COMPLETE WITHOUT AN ACCEPTABLE SITE DRAWING. |
| WV Department of Environmental Protection Division of Water and Waste Management Environmental Enforcement/ UST Unit http://www.dep.wv.gov/WWE/ee/ust/Pages/default.aspx 601 57th Street, S.E. Charleston, WV 25304 P (304) 926-0470 F (304) 926-0457 |

| CATHODIC PROTECTION — IMPRESSED CURRENT | Pg. 4 of 7 |
| --- | --- |
| XIII. IMPRESSED CURRENT CATHODIC PROTECTION SYSTEM CONTINUITY SURVEY |
| This section may be utilized to conduct measurements of continuity on underground storage tank systems that are protected by CP systems. When conducting a fixed cell – moving ground survey, the reference electrode must be placed in the soil at a remote location and left undisturbed. Conduct point-to-point test between any two structures for which the fixed cell-moving ground survey is inconclusive or indicates possible isolation. For impressed current systems, the protected structure must be continuous with all other protected structures in order to pass the continuity survey. |
| FACILITY NAME: |  | NOTE: The survey is not complete unless all other applicable parts of this form are also completed |
| DESCRIBE LOCATION OF “FIXED REMOTE” REFERENCE ELECTRODE PLACEMENT: |
| STRUCTURE “A” 1 | STRUCTURE “B” 2 | STRUCTURE “A” 3 FIXED REMOTE INSTANT OFF VOLTAGE | STRUCTURE “B” 4 FIXED REMOTE INSTANT OFF VOLTAGE | POINT-TO-POINT 5 VOLTAGE DIFFERENCE | ISOLATED/ 6 CONTINUOUS/ INCONCLUSIVE |
| (example) PLUS TANK BOTTOM | (example) PLUS STEEL PRODUCT LINE @ STP | (example) -915 mV | (example) -908 mV |  | (example) INCONCLUSIVE |
| (example) PLUS TANK BOTTOM | (example) PLUS STEEL PRODUCT LINE @ STP |  |  | (example) 1 mV | (example) CONTINUOUS |
| COMMENTS: |
| 1) Describe the cathodically protected structure {“A”} that you are trying to show is continuous (e.g., plus tank bottom). 2) Describe the “other” protected structure {“B”} that you are attempting to demonstrate is continuous (e.g., plus steel product line @ STP). 3) Record the fixed remote instant off structure-to-soil potential of the protected structure {“A”} in millivolts (e.g., -915 mV). 4) Record the fixed remote instant off structure-to-soil potential of the “other” protected structure {“B”} in millivolts (e.g., -908 mV). 5) Record the voltage observed between structure “A” and structure “B” when conducting “point-to-point” testing (e.g., 1 mV). 6) Document whether the test indicated the protected structure was isolated, continuous or inconclusive, according to the chart below. |
| Isolated Voltage difference is >10 mV | Continuous Voltage difference is ≤1 mV | Inconclusive Voltage difference is > 1 mV but ≤10 mV |
|  | WV Department of Environmental Protection Division of Water and Waste Management Environmental Enforcement/ UST Unit http://www.dep.wv.gov/WWE/ee/ust/Pages/default.aspx | 601 57th Street, S.E. Charleston, WV 25304 P (304) 926-0470 F (304) 926-0457 |  |
| CATHODIC PROTECTION — IMPRESSED CURRENT | Pg. 5 of 7 |
| XIIIb. IMPRESSED CURRENT CATHODIC PROTECTION SYSTEM CONTINUITY SURVEY-- Continued |
| STRUCTURE “A” 1 | STRUCTURE “B” 2 | STRUCTURE “A” 3 FIXED REMOTE INSTANT OFF VOLTAGE | STRUCTURE “B” 4 FIXED REMOTE INSTANT OFF VOLTAGE | POINT-TO-POINT 5 VOLTAGE DIFFERENCE | ISOLATED/ 6 CONTINUOUS/ INCONCLUSIVE |
| Additional Comments: |
| WV Department of Environmental Protection Division of Water and Waste Management Environmental Enforcement/ UST Unit http://www.dep.wv.gov/WWE/ee/ust/Pages/default.aspx 601 57th Street, S.E. Charleston, WV 25304 P (304) 926-0470 F (304) 926-0457 |  |
| CATHODIC PROTECTION — IMPRESSED CURRENT | Pg. 6 of 7 |
| XIV. CATHODIC PROTECTION SYSTEM SURVEY |
| This section may be used to conduct a survey of an impressed current protection system by obtaining structure-to-soil potential measurements. The reference electrode must be placed locally in a minimum of 3 locations in the soil directly over the tested structure and as far away from any active anode as practical to obtain a valid structure-to-soil potential. Both “on” and “instant off” potentials must be measured for each structure that is intended to be under cathodic protection. The “instant off” potential must be -850 mV or more negative or the 100 mV polarization criterion must be satisfied in order to pass. |
| FACILITY NAME: |  | NOTE: The survey is not complete unless all other applicable parts of this form are also completed |
| LOCATION CODE1 | STRUCTURE 2 | CONTACT POINT 3 | REFERENCE CELL PLACEMENT 4 | ON VOLTAGE5 | INSTANT OFF VOLTAGE6 | 100 mV POLARIZATION |  |
|  |  |  |  |  |  | ENDING VOLTAGE7 | VOLTAGE8 | PASS / FAIL9 |
| (example) T-1 | (example) PLUS TANK | (example) TANK BOTTOM | (example) SOIL @ REG. TANK STP MANWAY | (example) -1070mV | (example) -875 mV |  |  | (example) PASS |
| (example) P-2 | (example) DIESEL PIPING | (example) DISPENSER 7/8 | (example) SOIL @ DIESEL TANK STP MANWAY | (example) -810 mV | (example) -680 mV | (example) -575 mV | (example) -105 mV | (example) PASS |
| COMMENTS: |
| 1) Designate numerically or by code on the site drawing each “local” reference electrode placement (e.g., 1, 2, 3… T-1, T-2, P-1, P-2…etc.). 2) Describe the structure that is being tested (e.g., plus tank; premium piping; diesel submersible pump flex connector; etc.). 3) Describe where the structure being tested is contacted with the test lead (e.g., plus tank bottom; diesel piping @ dispenser 7/8; etc.). 4) Describe the exact location where reference electrode is placed for each measurement (e.g., soil @ regular tank STP manway; soil @ dispenser 2, etc.). 5) {Applies to all tests} Record the structure-to-soil potential (voltage) observed with the current applied (e.g., -1070 mV). 6) Record the structure-to-soil potential (voltage) observed when the current is interrupted (e.g., -680 mV). 7) {Applies to 100 mV polarization test only} Record the voltage observed at the end of the test period (e.g., -575 mV). 8) {Applies to 100 mV polarization test only} Subtract the ending voltage from the instant off voltage [e.g., -680mV - (-575 mV) = -105 mV]. 9) Indicate if the tested structure passed/failed one of the two acceptable criteria (-850 mV instant off or 100 mV polarization) based on your interpretation of data. |
|  | WV Department of Environmental Protection Division of Water and Waste Management Environmental Enforcement/ UST Unit http://www.dep.wv.gov/WWE/ee/ust/Pages/default.aspx | 601 57th Street, S.E. Charleston, WV 25304 P (304) 926-0470 F (304) 926-0457 |  |
| CATHODIC PROTECTION — IMPRESSED CURRENT | Pg. 7 of 7 |
| XIV. CATHODIC PROTECTION SYSTEM SURVEY-- Continued |
| LOCATION CODE1 | STRUCTURE 2 | CONTACT POINT 3 | REFERENCE CELL PLACEMENT 4 | ON VOLTAGE5 | INSTANT OFF VOLTAGE6 | 100 mV POLARIZATION | PASS / FAIL9 |
|  |  |  |  |  |  | ENDING VOLTAGE7 | VOLTAGE8 |  |
| Additional Comments: |
| IMPRESSED CURRENT CATHODIC PROTECTION SYSTEM 60-DAY RECORD OF RECTIFIER OPERATION |
| This form may be utilized to document that the cathodic protection system rectifier is checked for operation at least once every 60 days. Checked for operation is taken to mean that it was confirmed the rectifier was receiving power and is “turned-on”. Any significant variance should be reported to the corrosion professional so that any upgrades and/or adjustments necessary can be made. |
| UST OWNER | UST FACILITY |
| NAME: | NAME: | ID # |
| MAILING ADDRESS: |  | PHYSICAL ADDRESS: |  |
| CITY: | STATE: | CITY: | COUNTY: |
| IMPRESSED CURRENT RECTIFIER DATA |
| Rectifier Manufacturer: | Rated DC Output: VOLTS AMPS |
| Rectifier Model: | Rectifier Serial Number: |
| What is the ‘as designed’ or last recommended rectifier output? VOLTS AMPS |
| 60-DAY LOG OF RECTIFIER OPERATION |
| DATE INSPECTED | RECTIFIER TURNED ON? | TAP SETTINGS | DC OUTPUT | HOUR METER | INSPECTOR INITIALS | COMMENTS |
|  |  | COARSE | FINE | VOLTS | AMPS |  |  |  |