## Facility Summary
ESC Harrison County Power, LLC
Facility Emissions Summary Tables
Combustion Turbines/Duct Burners
Pollutant | Maximum Short Term Emissions: CT/DB | Maximum Annual Steady State Emissions: CT/DB | Startup and Shutdown Emissions: CT | Total Annual Emissions: CT/DB
| (lb/ hr ) | (tons/yr) | (tons/yr) | (tons/yr)
VOC | 11.4 | 49.932 | 4.846 | 54.778
NOx | 32.9 | 144.102 | 12.062 | 156.164
CO | 20 | 87.6 | 36.44 | 124.04
SO2 | 5.952 | 26.0698 | -- (1) | 26.0698
PM10/PM2.5 | 22.6 | 98.988 | 1.0894 | 100.0774
PM | 22.6 | 98.988 | 1.0894 | 100.0774
Pb | 0.0022047 | 0.0096564 | -- (1) | 0.0096564
H2SO4 | 3.824 | 16.7491 | -- (1) | 16.7491
(1)Worst-case annual emissions are addressed by steady-state operation.
Auxiliary Boiler
Pollutant | Maximum Short Term Emissions | Maximum Annual Emissions
| (lb/ hr ) | (tons/yr)
VOC | 0.62219 | 1.4236
NOx | 0.85551 | 1.9574
CO | 2.8776 | 6.584
SO2 | 0.086296 | 0.19744
PM10/PM2.5 | 0.60463 | 1.3834
PM | 0.60463 | 1.3834
Pb | 3.7754e-05 | 8.6382e-05
H2SO4 | 0.013214 | 0.030234
ESC Harrison County Power, LLC
Facility Emissions Summary Tables
Emergency Generator and Fire Water Pump
Pollutant | Emergency Generator Maximum Short Term Emissions | Emergency Generator Maximum Annual Emissions | Fire Water Pump Maximum Short Term Emissions | Fire Water Pump Maximum Annual Emissions
| (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr)
VOC | 0.65041 | 0.032521 | 0.05764 | 0.002882
NOx | 32.2249 | 1.6112 | 1.8681 | 0.093405
CO | 1.7738 | 0.088692 | 0.30556 | 0.015278
SO2 | 0.029187 | 0.0014594 | 0.0031725 | 0.00015862
PM10/PM2.5 | 0.14782 | 0.007391 | 0.051737 | 0.0025869
PM | 0.14782 | 0.007391 | 0.051737 | 0.0025869
Pb | -- | -- | -- | --
H2SO4 | 0.00018506 | 0.0035754 | 0.00038863 | 1.9432e-05
Fuel Gas Heater
Pollutant | Fuel Gas Heater Maximum Short Term Emissions | Fuel Gas Heater Maximum Annual Emissions
| (lb/hr) | (tons/yr)
VOC | 0.03829 | 0.16771
NOx | 0.19692 | 0.86252
CO | 0.21268 | 0.93152
SO2 | 0.0060694 | 0.026584
PM10/PM2.5 | 0.042525 | 0.18626
PM | 0.042525 | 0.18626
Pb | -- | --
H2SO4 | 0.00092938 | 0.0040707
ESC Harrison County Power, LLC
Facility Emissions Summary Tables
Facility-Wide Emissions Summary
Annual Emissions (tons/yr)
Unit | VOC | NOx | CO | SO2 | PM10 | PM | PM2.5 | Pb | H2SO4 | CO2e
CT/DB - Steady State | 49.932 | 144.102 | 87.6 | 26.0698 | 98.988 | 98.988 | 98.988 | 0.0096564 | 16.7491 | 2315019.9048
CT - Startups & Shutdowns | 4.846 | 12.062 | 36.44 | -- | 1.0894 | 1.0894 | 1.0894 | -- (1) | -- (1) | --
Auxiliary Boiler | 1.4236 | 1.9574 | 6.584 | 0.19744 | 1.3834 | 1.3834 | 1.3834 | 8.6382e-05 | 0.030234 | 20837.2162
Fuel Gas Heater | 0.16771 | 0.86252 | 0.93152 | 0.026584 | 0.18626 | 0.18626 | 0.18626 | -- | 0.0040707 | 2805.5331
Emergency Generator | 0.032521 | 1.6112 | 0.088692 | 0.0014594 | 0.007391 | 0.007391 | 0.007391 | -- | 0.0035754 | 158.0504
Fire Water Pump | 0.002882 | 0.093405 | 0.015278 | 0.00015862 | 0.0025869 | 0.0025869 | 0.0025869 | 0.00038863 | 1.9432e-05 | 17.1794
Circuit Breakers | -- | -- | -- | -- | -- | -- | -- | -- | -- | 58.425
Total | 56.4047 | 160.6886 | 131.6595 | 26.2954 | 101.657 | 101.657 | 101.657 | 0.010131 | 16.787 | 2338896.3089
Emission Calculations - GHGs
| CO2 |  | CH4 |  | N2O |  | SF6 |  | CO2e
Source | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr)
CT/DB | 528000 | 2312640 | 9.9153 | 43.4289 | 0.99153 | 4.3429 | -- | -- | 528543.3573 | 2315019.9048
Auxiliary Boiler | 9097.7788 | 20815.7179 | 0.17146 | 0.39231 | 0.017146 | 0.039231 | -- | -- | 9107.1749 | 20837.2162
Fuel Gas Heater | 639.8718 | 2802.6386 | 0.012059 | 0.05282 | 0.0012059 | 0.005282 | -- | -- | 640.5327 | 2805.5331
Emergency Generator | 3150.1974 | 157.5099 | 0.12778 | 0.006389 | 0.025556 | 0.0012778 | -- | -- | 3161.0076 | 158.0504
Fire Water Pump | 342.4128 | 17.1206 | 0.013889 | 0.00069446 | 0.0027778 | 0.00013889 | -- | -- | 343.5878 | 17.1794
Circuit Breakers | -- | -- | -- | -- | -- | -- | 0.00058505 | 0.0025625 | 13.339 | 58.425
Total CO2e | 541230.2608 | 2336432.987 | 10.2405 | 43.8811 | 1.0382 | 4.3888 | 0.00058505 | 0.0025625 | 541808.9992 | 2338896.3089
ESC Harrison County Power, LLC
Facility Emissions Summary Tables
Hazardous Air Pollutant (HAP) | CT (lb/hr) | DB (lb/hr) | Auxiliary Boiler (lb/hr) | Fuel Gas Heater (lb/hr) | Emergency Generator (lb/hr) | Fire Water Pump (lb/hr) | Facility Total (tons/yr)
2-Methylnaphthalene | NA | 2.3331e-06 | 1.8122e-06 | 1.2746e-07 | NA | NA | 1.4924e-05
Acetaldehyde | 0.013985 | NA | NA | NA | 0.00048686 | 0.0016107 | 0.061358
Acrolein | 0.0022376 | NA | NA | NA | 0.00015224 | 0.000788 | 0.0098093
Arsenic | NA | 0.00019443 | 1.5102e-05 | 1.0621e-06 | NA | NA | 0.0008908
Benzene | 0.0041954 | 0.00020415 | 0.00015857 | 1.1153e-05 | 0.014992 | 0.0019593 | 0.020529
Cadmium | NA | 0.0010693 | 8.306e-05 | 5.8418e-06 | NA | NA | 0.0048994
Chromium | NA | 0.001361 | 0.00010571 | 7.435e-06 | NA | NA | 0.0062356
Cobalt | NA | 8.1659e-05 | 6.3427e-06 | 4.461e-07 | NA | NA | 0.00037413
Dichlorobenzene | NA | 0.00011666 | 9.061e-05 | 6.3729e-06 | NA | NA | 0.00074618
Ethylbenzene | 0.011188 | NA | NA | NA | NA | NA | 0.049003
Fluoranthene | NA | 2.9164e-07 | 2.2653e-07 | 1.5932e-08 | NA | NA | 1.8655e-06
Fluorene | NA | 2.722e-07 | 2.1142e-07 | 1.487e-08 | NA | NA | 1.7411e-06
Formaldehyde | 1.0489 | 0.007291 | 0.0056632 | 0.00039831 | 0.0015243 | 0.002478 | 4.6408
Hexane | NA | 0.17498 | 0.13592 | 0.0095593 | NA | NA | 1.1193
Manganese | NA | 0.00036941 | 2.8693e-05 | 2.0181e-06 | NA | NA | 0.0016925
Mercury | NA | 0.00025276 | 1.9632e-05 | 1.3808e-06 | NA | NA | 0.001158
Naphthalene | 0.00045451 | 5.93e-05 | 4.606e-05 | 3.2395e-06 | 0.0025116 | 0.00017808 | 0.0025045
Nickel | NA | 0.0020415 | 0.00015857 | 1.1153e-05 | NA | NA | 0.0093534
Phenanathrene | NA | 1.6526e-06 | 1.2836e-06 | 9.0283e-08 | NA | NA | 1.0571e-05
POM | 0.00076916 | NA | NA | NA | 0.0040958 | 0.0003528 | 0.0035914
Pyrene | NA | 4.8607e-07 | 3.7754e-07 | 2.6554e-08 | NA | NA | 3.1091e-06
Toluene | 0.045451 | 0.00033053 | 0.00025673 | 1.8057e-05 | 0.0054289 | 0.0008589 | 0.2015
Xylenes | 0.022376 | NA | NA | NA | 0.0037288 | 0.0005985 | 0.098222
Maximum Emissions (Single HAP) | [6 empty] | 4.6408
Total HAPs | [6 empty] | 6.232
NA = No Emission Factor Available.
Global Warming Potential - CO2 | 1
Global Warming Potential - CH4 | 25
Global Warming Potential - N2O | 298
Global Warming Potential - SF6 | 22800

## CT - Steady State
ESC Harrison County Power, LLC
Emission Calculations - Combustion Turbine/Duct Burner | [6 empty] | Pre-Control Emissions
Input Data |  | Pollutant | CT/DB |  | CT/DB |  | Removal Efficiency | CT/DB
No. of Combustion Turbines | 1 |  | lb/hr | ton/yr(1) | mg/min | mg/m3 | % | lb/hr | ton/yr
Natural Gas Heating Value (Btu/lb - HHV) | 23482.1872 | VOC | 11.4 | 49.932 | 86182.48 | 1.7555 | 30% | 16.2857 | 71.3314
Natural Gas Heating Value (Btu/lb - LHV) | 21185.2219 | NOx | 32.9 | 144.102 | 248719.6133 | 5.0664 | 90% | 329 | 1441.02
LHV-HHV Conversion Factor (Natural Gas) | 1.1084 | CO | 20 | 87.6 | 151197.3333 | 3.0799 | 80% | 100 | 438
CT Annual Capacity Factor (%) | 100% | SO2 | 5.952 | 26.0698 | 44996.3264 | 0.91657 | 0% | 5.952 | 26.0698
CT Annual Operating Hours (hr/yr) | 8760 | PM/PM10/PM2.5 | 22.6 | 98.988 | 170852.9867 | 3.4803 | 0% | 22.6 | 98.988
Max. Heat Input, CT (MMBtu/hr) (HHV, all conditions) | 3496.2 | Pb(2) | 0.0022047 | 0.0096564 | 16.6669 | 0.0003395 | 0% | 0.0022047 | 0.0096564
Max. Heat Input, DB (MMBtu/hr) (HHV, all conditions) | 1001.3 | H2SO4(3) | 3.824 | 16.7491 | 28908.9301 | 0.58887 | 0% | 3.824 | 16.7491
Max. Heat Input CT + DB (MMBtu/hr) (HHV, all conditions) | 4497.5 | CO2(3) | 528000 | 2312640 | 3991609600 | 81308.8037 | 0% | 528000 | 2312640
Max. Heat Input CT + DB (MMBtu/yr) (HHV, all conditions) | 39398100 | CH4(4) | 9.9153 | 43.4289 | 74958.183 | 1.5269 | 0% | 9.9153 | 43.4289
Max. Natural Gas Use (ft3/hr) | 4366504.8544 | N2O(4) | 0.99153 | 4.3429 | 7495.8183 | 0.15269 | 0% | 0.99153 | 4.3429
Max. Natural Gas Use (MMft3/yr) | 38250.5825 | GHG (Mass Basis)(5) | 528010.9068 | 2312687.7718 | 3991692054.0013 | 81310.4833 | 0% | 528010.9068 | 2312687.7718
Pb Emission Factor (lb/MMscf) | 0.0005 | GHG (CO2e Basis)(6), (7) | 528543.3573 | 2315019.9048 | 3995717308.4309 | 81392.4774 | 0% | 528543.3573 | 2315019.9048
Global Warming Potential - CO2 | 1 | (1) Tons/yr = (Maximum lb/hr) x (8,760 hr/yr) x (1 ton/2000 lb).
Global Warming Potential - CH4 | 25 | (2) Pb emission factor from USEPA's AP-42, Section 1.4.
Global Warming Potential - N2O | 298 | (3) Based on the emissions and performance data provided by GE.
40 CFR Part 98 Subpart C Emission Factors for GHG Pollutants(4) |  | (4) Default emission factors obtained from 40 CFR Part 98, Subpart C: General Stationary Fuel Combustion Sources, Tables C-1 and C-2 for natural gas firing.
| Natural Gas | (5) The sum of potential annual GHG emissions on a mass basis (i.e., no GWP applied).
Conversion Factor (kg to lb) | 2.2046 | (6) For each GHG, emissions are normalized to a CO2e basis by multiplying the mass emissions of each individual GHG pollutant by its respective Global warming potentials (GWP). GWP of each pollutant established by 40 CFR Part 98, Subpart A: General Provisions, Table A-1.
CO2 Emission Factor (kg/MMBtu) | 53.06
CO2 Emission Factor (lb/MMBtu) | 116.9771
CH4 Emission Factor (kg/MMBtu) | 0.001 | (7) The sum of potential annual GHG emissions on a CO2e basis.
CH4 Emission Factor (lb/MMBtu) | 0.0022046
N2O Emission Factor (kg/MMBtu) | 0.0001
N2O Emission Factor (lb/MMBtu) | 0.00022046

## CT Startups&Shutdowns
ESC Harrison County Power, LLC
Emission Calculations - Combustion Turbine Startups and Shutdowns
Type | Pollutant | Emissions (lb/event)(1) | Duration (min/event)(1) | No. of Events per Year(1) | Total Duration (hr/yr) | Emissions (lb/yr) | Emissions from 1 CT (tons/yr)
NOx
Startups | Hot | 67 | 20 | 208 | 69.3333 | 13936 | 6.968
| Warm | 130 | 40 | 40 | 26.6667 | 5200 | 2.6
| Cold | 264 | 55 | 12 | 11 | 3168 | 1.584
Shutdowns |  | 7 | 12 | 260 | 52 | 1820 | 0.91
| Total |  |  |  | 159 | 24124 | 12.062
CO
Startups | Hot | 120 | 20 | 208 | 69.3333 | 24960 | 12.48
| Warm | 155 | 40 | 40 | 26.6667 | 6200 | 3.1
| Cold | 790 | 55 | 12 | 11 | 9480 | 4.74
Shutdowns |  | 124 | 12 | 260 | 52 | 32240 | 16.12
| Total |  |  |  | 159 | 72880 | 36.44
VOC (as Methane)
Startups | Hot | 9 | 20 | 208 | 69.3333 | 1872 | 0.936
| Warm | 10 | 40 | 40 | 26.6667 | 400 | 0.2
| Cold | 55 | 55 | 12 | 11 | 660 | 0.33
Shutdowns |  | 26 | 12 | 260 | 52 | 6760 | 3.38
| Total |  |  |  | 159 | 9692 | 4.846
PM/PM10/PM2.5
Startups | Hot | 4.6 | 20 | 208 | 69.3333 | 956.8 | 0.4784
| Warm | 9.1 | 40 | 40 | 26.6667 | 364 | 0.182
| Cold | 13 | 55 | 12 | 11 | 156 | 0.078
Shutdowns |  | 2.7 | 12 | 260 | 52 | 702 | 0.351
| Total |  |  |  | 159 | 2178.8 | 1.0894
(1) Startup and shutdown emission rates obtained from GE performance data.
(2) Startup and shutdown emission rates were not calculated for SO2, Pb, H2SO4, or GHGs. Worst-case emissions for those pollutants were assumed to be from steady-state operation.

## Auxiliary Boiler
ESC Harrison County Power, LLC
Emission Calculations - Auxiliary Boiler
Parameter | Value
Natural Gas Heating Value (Btu/scf) | 1030
Maximum Heat Input (MMBtu/hr): | 77.774
Maximum Heat Input (Btu/hr) | 77773990.7256
Maximum Hourly Fuel Use (scf/hr) | 75508.7289
Maximum Hourly Fuel Use (MMscf/hr) | 0.075509
Maximum Annual Fuel Use (MMscf/yr) | 345.5279
Maximum Annual Fuel Use (MMBtu/yr) | 355893.7816
Maximum Annual Operation (hr/yr) | 4576
Natural Gas Percentage of Fuel Blend | 100%
Fuel Sulfur Content (gr/100 scf) | 0.4
Conversion Factor (gr/lb) | 7000
Conversion Factor SO2 to SO3 | 10%
Conversion Factor SO3 to H2SO4 | 100%
Molecular weight of S | 32
Molecular weight of SO2 | 64
Molecular weight of SO3 | 80
Molecular weight of H2SO4 | 98
Global Warming Potential - CO2 | 1
Global Warming Potential - CH4 | 25
Global Warming Potential - N2O | 298
40 CFR Part 98 Subpart C Emission Factors for GHG Pollutants(5)
Natural Gas
Conversion Factor (kg to lb) | 2.2046
CO2 Emission Factor (kg/MMBtu) | 53.06
CO2 Emission Factor (lb/MMBtu) | 116.9771
CH4 Emission Factor (kg/MMBtu) | 0.001
CH4 Emission Factor (lb/MMBtu) | 0.0022046
N2O Emission Factor (kg/MMBtu) | 0.0001
N2O Emission Factor (lb/MMBtu) | 0.00022046 |  |  |  |  | Pre-Control Emissions
[6 empty] | Removal Efficiency | Aux Boiler
Pollutant | Emission Factor (lb/MMBtu)(2, 5) | Emissions (lb/hr) | Emissions (tons/yr) | Emissions (mg/min) | Emissions (mg/m3) | % | lb/hr | ton/yr
VOC | 0.008 | 0.62219 | 1.4236 | 4703.688 | 11.9969 | 0% | 0.62219 | 1.4236
NOx | 0.011 | 0.85551 | 1.9574 | 6467.571 | 16.4957 | 0% | 0.85551 | 1.9574
CO | 0.037 | 2.8776 | 6.584 | 21754.557 | 55.4857 | 0% | 2.8776 | 6.584
SO2 (3) | 0.0011096 | 0.086296 | 0.19744 | 652.3839 | 1.6639 | 0% | 0.086296 | 0.19744
PM (1)/PM10/PM2.5 | 0.0077741 | 0.60463 | 1.3834 | 4570.8916 | 11.6582 | 0% | 0.60463 | 1.3834
Pb | 4.8544e-07 | 3.7754e-05 | 8.6382e-05 | 0.28542 | 0.00072797 | 0% | 3.7754e-05 | 8.6382e-05
H2SO4(4) | 0.0001699 | 0.013214 | 0.030234 | 99.8963 | 0.25479 | 0% | 0.013214 | 0.030234
CO2 (5) | 116.9771 | 9097.7788 | 20815.7179 | 68777994.5676 | 175420.4793 | 0% | 9097.7788 | 20815.7179
CH4 (5) | 0.0022046 | 0.17146 | 0.39231 | 1296.2306 | 3.3061 | 0% | 0.17146 | 0.39231
N2O (5) | 0.00022046 | 0.017146 | 0.039231 | 129.6231 | 0.33061 | 0% | 0.017146 | 0.039231
GHG (Mass Basis) (6) | -- | 9097.9674 | 20816.1494 | 68779420.4212 | 175424.116 | 0% | 9097.9674 | 20816.1494
GHG (CO2e Basis) (7, 8) | -- | 9107.1749 | 20837.2162 | 68849028.0034 | 175601.6523 | 0% | 9107.1749 | 20837.2162
(1) PM emission factor includes filterable and condensable fractions.
(2) Emission factors obtained from potential vendor.
(3) SO2 lb/hr emission rate calculated as a mass balance and based on fuel consumption and fuel sulfur content.
(4) Exhaust emissions are based on 95% fuel sulfur conversion to SO2 and 5% fuel sulfur conversion to SO3. Sulfuric acid mist (H2SO4) emission calculations conservatively assume that all SO3 combines with water to form sulfur mist. SO3 = SO2 emissions (lb/hr) * 5% * MW SO3/MW SO2 H2SO4 = SO3 emissions (lb/hr) * 100% * MW H2SO4/MW SO3
(5) Default emission factors obtained from 40 CFR Part 98, Subpart C: General Stationary Fuel Combustion Sources, Tables C-1 and C-2 for natural gas firing and ethane combustion. Per Table C-2, the default CH4 and N2O factors for ethane combustion are those for "Petroleum".
(6) The sum of potential annual GHG emissions on a mass basis (i.e., no GWP applied).
(7) For each GHG, emissions are normalized to a CO2e basis by multiplying the mass emissions of each individual GHG pollutant by its respective Global warming potentials (GWP). GWP of each pollutant established by 40 CFR Part 98, Subpart A: General Provisions, Table A-1.
(8) The sum of potential annual GHG emissions on a CO2e basis.
Hazardous Air Pollutants
Pollutant | Emission Factor (lb/MMscf) (1) | Emissions (lb/hr) | Emissions (tons/yr) | Emissions (mg/min)(2) | Emissions (mg/m3)(3)
2-Methylnaphthalene | 2.4e-05 | 1.8122e-06 | 4.1463e-06 | 0.0137 | 3.4942e-05
Arsenic | 0.0002 | 1.5102e-05 | 3.4553e-05 | 0.11417 | 0.00029119
Benzene | 0.0021 | 0.00015857 | 0.0003628 | 1.1988 | 0.0030575
Cadmium | 0.0011 | 8.306e-05 | 0.00019004 | 0.62792 | 0.0016015
Chromium | 0.0014 | 0.00010571 | 0.00024187 | 0.79917 | 0.0020383
Cobalt | 8.4e-05 | 6.3427e-06 | 1.4512e-05 | 0.04795 | 0.0001223
Dichlorobenzene | 0.0012 | 9.061e-05 | 0.00020732 | 0.685 | 0.0017471
Fluoranthene | 3e-06 | 2.2653e-07 | 5.1829e-07 | 0.0017125 | 4.3678e-06
Fluorene | 2.8e-06 | 2.1142e-07 | 4.8374e-07 | 0.0015983 | 4.0766e-06
Formaldehyde | 0.075 | 0.0056632 | 0.012957 | 42.8127 | 0.1092
Hexane | 1.8 | 0.13592 | 0.31098 | 1027.5047 | 2.6207
Manganese | 0.00038 | 2.8693e-05 | 6.565e-05 | 0.21692 | 0.00055326
Mercury | 0.00026 | 1.9632e-05 | 4.4919e-05 | 0.14842 | 0.00037854
Naphthalene | 0.00061 | 4.606e-05 | 0.00010539 | 0.34821 | 0.00088812
Nickel | 0.0021 | 0.00015857 | 0.0003628 | 1.1988 | 0.0030575
Phenanathrene | 1.7e-05 | 1.2836e-06 | 2.937e-06 | 0.0097042 | 2.4751e-05
Pyrene | 5e-06 | 3.7754e-07 | 8.6382e-07 | 0.0028542 | 7.2797e-06
Toluene | 0.0034 | 0.00025673 | 0.0005874 | 1.9408 | 0.0049502
(1) Emission factors obtained from AP-42, Ch. 1.4, Tables 1.4-3 and 1.4-4. Emission factors were not included for pollutants at or below the method detection limits, designated as "less than (<)" in AP-42 emission factor tables.
(2) Grams per Pound Conversion Factor | 453.592
(3) Based on stack exhaust flow rate of (ACFM) | 13846

## Fuel Gas Heater
ESC Harrison County Power, LLC
Emission Calculations - Fuel Gas Heater
Parameter | Value
Natural Gas Heating Value (Btu/scf) | 1030
Maximum Heat Input (MMBtu/hr): | 5.4701
Maximum Heat Input (Btu/hr) | 5470058.8714
Maximum Annual Fuel Use (scf/hr) | 5310.7368
Maximum Annual Fuel Use (MMscf/hr) | 0.0053107
Maximum Annual Fuel Use (MMscf/yr) | 46.5221
Maximum Annual Fuel Use (MMBtu/yr) | 47917.7157
Maximum Annual Operation (hr/yr) | 8760
Natural Gas Percentage of Fuel Blend | 100%
Fuel Sulfur Content (gr/100 scf) | 0.4
Conversion Factor (gr/lb) | 7000
Conversion Factor SO2 to SO3 | 10%
Conversion Factor SO3 to H2SO4 | 100%
Molecular weight of S | 32
Molecular weight of SO2 | 64
Molecular weight of SO3 | 80
Molecular weight of H2SO4 | 98
Global Warming Potential - CO2 | 1
Global Warming Potential - CH4 | 25
Global Warming Potential - N2O | 298
40 CFR Part 98 Subpart C Emission Factors for GHG Pollutants(5)
Natural Gas
Conversion Factor (kg to lb) | 2.2046
CO2 Emission Factor (kg/MMBtu) | 53.06
CO2 Emission Factor (lb/MMBtu) | 116.9771
CH4 Emission Factor (kg/MMBtu) | 0.001
CH4 Emission Factor (lb/MMBtu) | 0.0022046
N2O Emission Factor (kg/MMBtu) | 0.0001
N2O Emission Factor (lb/MMBtu) | 0.00022046
Pollutant | Emission Factor (lb/MMBtu)(2, 5) | Emissions (lb/hr) | Emissions (tons/yr) | Emissions (mg/min) | Emissions (mg/m3)
VOC | 0.007 | 0.03829 | 0.16771 | 289.4704 | 10.5062
NOx | 0.036 | 0.19692 | 0.86252 | 1488.705 | 3.797
CO | 0.03888 | 0.21268 | 0.93152 | 1607.8014 | 4.1007
SO2 (3) | 0.0011096 | 0.0060694 | 0.026584 | 45.884 | 0.11703
PM (1)/PM10/PM2.5 | 0.0077741 | 0.042525 | 0.18626 | 321.4834 | 0.81995
Pb | 4.8544e-07 | 2.6554e-06 | 1.1631e-05 | 0.020074 | 5.12e-05
H2SO4(4) | 0.0001699 | 0.00092938 | 0.0040707 | 7.026 | 0.01792
CO2 (5) | 116.9771 | 639.8718 | 2802.6386 | 4837345.6966 | 12337.8052
CH4 (5) | 0.0022046 | 0.012059 | 0.05282 | 91.1675 | 0.23253
N2O (5) | 0.00022046 | 0.0012059 | 0.005282 | 9.1167 | 0.023253
GHG (Mass Basis) (6) | -- | 639.8851 | 2802.6967 | 4837445.9808 | 12338.061
GHG (CO2e Basis) (7, 8) | -- | 640.5327 | 2805.5331 | 4842341.6737 | 12350.5476
(1) PM emission factor includes filterable and condensable fractions.
(2) Emission factors obtained from potential vendor.
(3) SO2 lb/hr emission rate calculated as a mass balance and based on fuel consumption and fuel sulfur content.
(4) Exhaust emissions are based on 95% fuel sulfur conversion to SO2 and 5% fuel sulfur conversion to SO3. Sulfuric acid mist (H2SO4) emission calculations conservatively assume that all SO3 combines with water to form sulfur mist. SO3 = SO2 emissions (lb/hr) * 5% * MW SO3/MW SO2 H2SO4 = SO3 emissions (lb/hr) * 100% * MW H2SO4/MW SO3
(5) Default emission factors obtained from 40 CFR Part 98, Subpart C: General Stationary Fuel Combustion Sources, Tables C-1 and C-2 for natural gas firing and ethane combustion. Per Table C-2, the default CH4 and N2O factors for ethane combustion are those for "Petroleum".
(6) The sum of potential annual GHG emissions on a mass basis (i.e., no GWP applied).
(7) For each GHG, emissions are normalized to a CO2e basis by multiplying the mass emissions of each individual GHG pollutant by its respective Global warming potentials (GWP). GWP of each pollutant established by 40 CFR Part 98, Subpart A: General Provisions, Table A-1.
(8) The sum of potential annual GHG emissions on a CO2e basis.
Hazardous Air Pollutants
Pollutant | Emission Factor (lb/MMscf) (1) | Emissions (lb/hr) | Emissions (tons/yr) | Emissions (mg/min)(2) | Emissions (mg/m3)(3)
2-Methylnaphthalene | 2.4e-05 | 1.2746e-07 | 5.5826e-07 | 0.00096356 | 3.4972e-05
Arsenic | 0.0002 | 1.0621e-06 | 4.6522e-06 | 0.0080297 | 0.00029143
Benzene | 0.0021 | 1.1153e-05 | 4.8848e-05 | 0.084312 | 0.0030601
Cadmium | 0.0011 | 5.8418e-06 | 2.5587e-05 | 0.044163 | 0.0016029
Chromium | 0.0014 | 7.435e-06 | 3.2565e-05 | 0.056208 | 0.00204
Cobalt | 8.4e-05 | 4.461e-07 | 1.9539e-06 | 0.0033725 | 0.0001224
Dichlorobenzene | 0.0012 | 6.3729e-06 | 2.7913e-05 | 0.048178 | 0.0017486
Fluoranthene | 3e-06 | 1.5932e-08 | 6.9783e-08 | 0.00012045 | 4.3715e-06
Fluorene | 2.8e-06 | 1.487e-08 | 6.5131e-08 | 0.00011242 | 4.0801e-06
Formaldehyde | 0.075 | 0.00039831 | 0.0017446 | 3.0111 | 0.10929
Hexane | 1.8 | 0.0095593 | 0.04187 | 72.2672 | 2.6229
Manganese | 0.00038 | 2.0181e-06 | 8.8392e-06 | 0.015256 | 0.00055373
Mercury | 0.00026 | 1.3808e-06 | 6.0479e-06 | 0.010439 | 0.00037887
Naphthalene | 0.00061 | 3.2395e-06 | 1.4189e-05 | 0.024491 | 0.00088888
Nickel | 0.0021 | 1.1153e-05 | 4.8848e-05 | 0.084312 | 0.0030601
Phenanathrene | 1.7e-05 | 9.0283e-08 | 3.9544e-07 | 0.00068252 | 2.4772e-05
Pyrene | 5e-06 | 2.6554e-08 | 1.1631e-07 | 0.00020074 | 7.2859e-06
Toluene | 0.0034 | 1.8057e-05 | 7.9087e-05 | 0.1365 | 0.0049544
(1) Emission factors obtained from AP-42, Ch. 1.4, Tables 1.4-3 and 1.4-4. Emission factors were not included for pollutants at or below the method detection limits, designated as "less than (<)" in AP-42 emission factor tables.
(2) Grams per Pound Conversion Factor | 453.592
(3) Based on stack exhaust flow rate of (ACFM) | 973

## Emergency Generator
ESC Harrison County Power, LLC
Emission Calculations - Emergency Generator (Tier 2)
Parameter | Value
Heating Value of ULSD (Btu/gal): | 140000
ULSD Sulfur Content (wt. %): | 0.0015
Rated Output (kW): | 2000
Rated Output (hp): | 2682
Fuel Consumption (gal/hr): | 138
Heat Input (MMBtu/hr): | 19.32
Maximum Annual Operation (hr/yr) | 100
NOx + NMHC Emission Factor (g/hp-hr) | 2.8
Concentration of NOx | 90%
Concentration of NMHC | 10%
Conversion Factor SO2 to SO3 | 10%
Conversion Factor SO3 to H2SO4 | 100%
Molecular weight of S | 32
Molecular weight of SO2 | 64
Molecular weight of SO3 | 80
Molecular weight of H2SO4 | 98
Fuel Oil Density (lb/gal) | 7.05
kg-lb Conversion Factor | 2.2046
CO2 Emission Factor (kg/MMBtu) | 73.96
CO2 Emission Factor (lb/MMBtu) | 163.0537
CH4 Emission Factor (kg/MMBtu) | 0.003
CH4 Emission Factor (lb/MMBtu) | 0.0066139
N2O Emission Factor (kg/MMBtu) | 0.0006
N2O Emission Factor (lb/MMBtu) | 0.0013228
Global Warming Potential - CO2 | 1
Global Warming Potential - CH4 | 25
Global Warming Potential - N2O | 298
Criteria Pollutants
Pollutant | Emission Factor (g/hp-hr) (1) | Emission Factor (lb/MMBtu) | Emissions (lb/hr) | Emissions (tons/yr) | Emissions (mg/min) | Emissions (mg/m3)
VOC | 0.11 | -- | 0.65041 | 0.032521 | 4917.0217 | 22.7058
NOx | 5.45 | -- | 32.2249 | 1.6112 | 243616.0742 | 1124.9716
CO | 0.3 | -- | 1.7738 | 0.088692 | 13410.0591 | 61.925
SO2 | -- | -- | 0.029187 | 0.0014594 | 220.6498 | 1.0189
PM/PM10/PM2.5 | 0.025 | -- | 0.14782 | 0.007391 | 1117.5049 | 5.1604
H2SO4(4) | -- | 0.00018506 | 0.0035754 | 0.00017877 | 27.0296 | 0.12482
CO2 | -- | 163.0537 | 3150.1974 | 157.5099 | 23815072.2516 | 109973.369
CH4 | -- | 0.0066139 | 0.12778 | 0.006389 | 965.9981 | 4.4608
N2O | -- | 0.0013228 | 0.025556 | 0.0012778 | 193.1996 | 0.89216
GHG (Mass Basis) | -- | -- | 3150.3507 | 157.5175 | 23816231.4493 | 109978.722
GHG (CO2e Basis) | -- | -- | 3161.0076 | 158.0504 | 23896795.6878 | 110350.7519
(1) Emission factors NOx, CO, PM, and VOC provided by vendor. SO2 lb/hr emission rate calculated as a mass balance and based on fuel consumption and fuel oil sulfur content.
(2) Default emission factors obtained from 40 CFR Part 98, Subpart C: General Stationary Fuel Combustion Sources, Tables C-1 and C-2 for distillate fuel oil No. 2 firing.
(3) Global warming potentials (GWP) of each pollutant established by 40 CFR Part 98, Subpart A: General Provisions, Table A-1.
(4) For each GHG, emissions are normalized to a CO2e basis by multiplying the mass emissions of each individual GHG pollutant by its respective GWP.
(5) The sum of potential annual GHG emissions on a mass basis (i.e., no GWP applied).
(6) The sum of potential annual GHG emissions on a CO2e basis.
Hazardous Air Pollutants
Pollutant | Emission Factor (lb/MMBtu)(1), (2) | Emissions (lb/hr) | Emissions (tons/yr) | Emissions (mg/min)(3) | Emissions (mg/m3)(4)
Acetaldehyde | 2.52e-05 | 0.00048686 | 2.4343e-05 | 3.6806 | 0.016996
Acrolein | 7.88e-06 | 0.00015224 | 7.6121e-06 | 1.1509 | 0.0053148
Benzene | 0.000776 | 0.014992 | 0.00074962 | 113.3399 | 0.52338
Formaldehyde | 7.89e-05 | 0.0015243 | 7.6217e-05 | 11.5239 | 0.053215
Naphthalene | 0.00013 | 0.0025116 | 0.00012558 | 18.9874 | 0.08768
POM | 0.000212 | 0.0040958 | 0.00020479 | 30.964 | 0.14299
Toluene | 0.000281 | 0.0054289 | 0.00027145 | 41.0419 | 0.18952
Xylenes | 0.000193 | 0.0037288 | 0.00018644 | 28.1889 | 0.13017
(1) Emission factors provided AP-42, Tables 3.4-3 and 3.4-4 Emission factors were not included for pollutants at or below the method detection limits, designated as "less than (<)" in AP-42 emission factor tables.
(2) Polycyclic Organic Matter (listed as "Total PAH" in AP-42)
(3) Grams per Pound Conversion Factor | 453.592
(4) Based on stack exhaust flow rate of (ACFM) | 15295

## Fire Water Pump
ESC Harrison County Power, LLC
Emission Calculations - Fire Water Pump (Tier 2)
Parameter | Value
Heating Value of ULSD (Btu/gal): | 140000
ULSD Sulfur Content (wt. %): | 0.0015
Rated Output (hp): | 315
Fuel Consumption (gal/hr): | 15
Heat Input (MMBtu/hr): | 2.1
Maximum Annual Operation (hr/yr): | 100
NOx + NMHC Emission Factor (g/hp-hr) | 3
Concentration of NOx | 90%
Concentration of NMHC | 10%
Conversion Factor SO2 to SO3 | 10%
Conversion Factor SO3 to H2SO4 | 100%
Molecular weight of S | 32
Molecular weight of SO2 | 64
Molecular weight of SO3 | 80
Molecular weight of H2SO4 | 98
Fuel Oil Density (lb/gal) | 7.05
kg-lb Conversion Factor | 2.2046
CO2 Emission Factor (kg/MMBtu) | 73.96
CO2 Emission Factor (lb/MMBtu) | 163.0537
CH4 Emission Factor (kg/MMBtu) | 0.003
CH4 Emission Factor (lb/MMBtu) | 0.0066139
N2O Emission Factor (kg/MMBtu) | 0.0006
N2O Emission Factor (lb/MMBtu) | 0.0013228
Global Warming Potential - CO2 | 1
Global Warming Potential - CH4 | 25
Global Warming Potential - N2O | 298
Criteria Pollutants
Pollutant | Emission Factor (g/hp-hr)(1) | Emission Factor (lb/MMBtu) | Emissions (lb/hr) | Emissions (tons/yr) | Emissions (mg/min) | Emissions (mg/m3)
VOC | 0.083 | -- | 0.05764 | 0.002882 | 435.7519 | 10.9917
NOx | 2.69 | -- | 1.8681 | 0.093405 | 14122.5623 | 356.2383
CO | 0.44 | -- | 0.30556 | 0.015278 | 2310.0102 | 58.2695
SO2 | -- | -- | 0.0031725 | 0.00015862 | 23.9837 | 0.60498
PM/PM10/PM2.5 | 0.0745 | -- | 0.051737 | 0.0025869 | 391.1267 | 9.8661
H2SO4(4) |  | 0.00018506 | 0.00038863 | 1.9432e-05 | 2.938 | 0.07411
CO2 | -- | 163.0537 | 342.4128 | 17.1206 | 2588594.81 | 65296.6879
CH4 | -- | 0.0066139 | 0.013889 | 0.00069446 | 104.9998 | 2.6486
N2O | -- | 0.0013228 | 0.0027778 | 0.00013889 | 21 | 0.52972
GHG (Mass Basis) | -- | -- | 342.4294 | 17.1215 | 2588720.8097 | 65299.8662
GHG (CO2e Basis) | -- | -- | 343.5878 | 17.1794 | 2597477.7922 | 65520.759
(1) Emission factors NOx, CO, PM, and VOC provided by vendor. SO2 lb/hr emission rate calculated as a mass balance and based on fuel consumption and fuel oil sulfur content.
(2) Default emission factors obtained from 40 CFR Part 98, Subpart C: General Stationary Fuel Combustion Sources, Tables C-1 and C-2 for distillate fuel oil No. 2 firing.
(3) Global warming potentials (GWP) of each pollutant established by 40 CFR Part 98, Subpart A: General Provisions, Table A-1.
(4) For each GHG, emissions are normalized to a CO2e basis by multiplying the mass emissions of each individual GHG pollutant by its respective GWP.
(5) The sum of potential annual GHG emissions on a mass basis (i.e., no GWP applied).
(6) The sum of potential annual GHG emissions on a CO2e basis.
Hazardous Air Pollutants
Pollutant | Emission Factor (lb/MMBtu)(1), (2) | Emissions (lb/hr) | Emissions (tons/yr) | Emissions (mg/min)(3) | Emissions (mg/m3)(4)
Acetaldehyde | 0.000767 | 0.0016107 | 8.0535e-05 | 12.1767 | 0.30715
Acrolein | 7.88e-06 | 0.000788 | 1.182e-06 | 18.3867 | 0.042453
Benzene | 0.000933 | 0.0019593 | 9.7965e-05 | 14.812 | 0.37363
Formaldehyde | 0.00118 | 0.002478 | 0.0001239 | 18.7333 | 0.47254
Naphthalene | 8.48e-05 | 0.00017808 | 8.904e-06 | 1.3463 | 0.033959
POM | 0.000168 | 0.0003528 | 1.764e-05 | 2.6671 | 0.067277
Toluene | 0.000409 | 0.0008589 | 4.2945e-05 | 6.4932 | 0.16379
Xylenes | 0.000285 | 0.0005985 | 2.9925e-05 | 4.5246 | 0.11413
(1) Emission factors obtained from AP-42, Ch. 3.3, Table 3.3-2. Emission factors were not included for pollutants at or below the method detection limits, designated as "less than (<)" in AP-42 emission factor tables.
(2) Polycyclic Organic Matter (listed as "Total PAH" in AP-42)
(3) Grams per Pound Conversion Factor | 453.592
(4) Based on stack exhaust flow rate of (ACFM) | 1400

## Project HAPS
ESC Harrison County Power, LLC
Emission Calculations - HAPs
Parameters | Units | CT | DB | Auxiliary Boiler | Fuel Gas Heater | Emergency Generator | Fire Water Pump | CT Organic HAP Control Efficiency(3) |  | Emission Concentrations for Attachment J
Maximum Heat Input | MMBtu/hr | 3496.2 | 1001.3 | 77.774 | 5.4701 | 19.32 | 2.1 | 90%
Maximum Annual Operation | hr/yr | 8760 | 8760 | 4576 | 8760 | 100 | 100 |  |  | Conversions | g/lb | 453.592
[11 empty] | m/ft | 0.3048
HAP | CT Emission Factor(1) (lb/MMBtu) | DB Emission Factor (2) (lb/MMscf) | One CT (lb/hr) | One DB (lb/hr) | One CT + One DB (lb/hr) | One CT (tons/yr) | One DB (tons/yr) | One CT + One DB (tons/yr) | One CT mg/min | One CT mg/m3 | One DB mg/min | One DB mg/m3 | One CT + One DB mg/m3 | UncontrolledOne CT (lb/hr) | UncontrolledOne DB (lb/hr) | Uncontrolled One CT + One DB (lb/hr) | Uncontrolled One CT + One DB (ton/yr)
2-Methylnaphthalene | NA | 2.4e-05 | NA | 2.3331e-06 | 2.3331e-06 | NA | 1.0219e-05 | 1.0219e-05 | NA | NA | 0.017638 | 3.5929e-07 | 3.5929e-07 | NA | 2.3331e-05 | 2.3331e-05 | 0.00010219
Acetaldehyde | 4e-05 | NA | 0.013985 | NA | 0.013985 | 0.061253 | NA | 0.061253 | 105.7232 | 0.0021536 | NA | NA | 0.0021536 | 0.13985 | NA | 0.13985 | 0.61253
Acrolein | 6.4e-06 | NA | 0.0022376 | NA | 0.0022376 | 0.0098005 | NA | 0.0098005 | 16.9157 | 0.00034457 | NA | NA | 0.00034457 | 0.022376 | NA | 0.022376 | 0.098005
Arsenic | NA | 0.0002 | NA | 0.00019443 | 0.00019443 | NA | 0.00085159 | 0.00085159 | NA | NA | 1.4698 | 2.9941e-05 | 2.9941e-05 | NA | 0.00019443 | 0.00019443 | 0.00085159
Benzene | 1.2e-05 | 0.0021 | 0.0041954 | 0.00020415 | 0.0043996 | 0.018376 | 0.00089417 | 0.01927 | 31.717 | 0.00064607 | 1.5433 | 3.1438e-05 | 0.00067751 | 0.041954 | 0.0020415 | 0.043996 | 0.1927
Cadmium | NA | 0.0011 | NA | 0.0010693 | 0.0010693 | NA | 0.0046838 | 0.0046838 | NA | NA | 8.0841 | 0.00016467 | 0.00016467 | NA | 0.0010693 | 0.0010693 | 0.0046838
Chromium | NA | 0.0014 | NA | 0.001361 | 0.001361 | NA | 0.0059611 | 0.0059611 | NA | NA | 10.2889 | 0.00020958 | 0.00020958 | NA | 0.001361 | 0.001361 | 0.0059611
Cobalt | NA | 8.4e-05 | NA | 8.1659e-05 | 8.1659e-05 | NA | 0.00035767 | 0.00035767 | NA | NA | 0.61733 | 1.2575e-05 | 1.2575e-05 | NA | 8.1659e-05 | 8.1659e-05 | 0.00035767
Dichlorobenzene | NA | 0.0012 | NA | 0.00011666 | 0.00011666 | NA | 0.00051095 | 0.00051095 | NA | NA | 0.88191 | 1.7964e-05 | 1.7964e-05 | NA | 0.0011666 | 0.0011666 | 0.0051095
Ethylbenzene | 3.2e-05 | NA | 0.011188 | NA | 0.011188 | 0.049003 | NA | 0.049003 | 84.5786 | 0.0017229 | NA | NA | 0.0017229 | 0.11188 | NA | 0.11188 | 0.49003
Fluoranthene | NA | 3e-06 | NA | 2.9164e-07 | 2.9164e-07 | NA | 1.2774e-06 | 1.2774e-06 | NA | NA | 0.0022048 | 4.4911e-08 | 4.4911e-08 | NA | 2.9164e-06 | 2.9164e-06 | 1.2774e-05
Fluorene | NA | 2.8e-06 | NA | 2.722e-07 | 2.722e-07 | NA | 1.1922e-06 | 1.1922e-06 | NA | NA | 0.0020578 | 4.1917e-08 | 4.1917e-08 | NA | 2.722e-06 | 2.722e-06 | 1.1922e-05
Formaldehyde | 0.0003 | 0.075 | 1.0489 | 0.007291 | 1.0562 | 4.594 | 0.031935 | 4.6259 | 7929.2418 | 0.16152 | 55.1191 | 0.0011228 | 0.16264 | 10.4886 | 0.07291 | 10.5615 | 46.2594
Hexane | NA | 1.8 | NA | 0.17498 | 0.17498 | NA | 0.76643 | 0.76643 | NA | NA | 1322.8592 | 0.026947 | 0.026947 | NA | 1.7498 | 1.7498 | 7.6643
Manganese | NA | 0.00038 | NA | 0.00036941 | 0.00036941 | NA | 0.001618 | 0.001618 | NA | NA | 2.7927 | 5.6887e-05 | 5.6887e-05 | NA | 0.00036941 | 0.00036941 | 0.001618
Mercury | NA | 0.00026 | NA | 0.00025276 | 0.00025276 | NA | 0.0011071 | 0.0011071 | NA | NA | 1.9108 | 3.8923e-05 | 3.8923e-05 | NA | 0.00025276 | 0.00025276 | 0.0011071
Naphthalene | 1.3e-06 | 0.00061 | 0.00045451 | 5.93e-05 | 0.00051381 | 0.0019907 | 0.00025974 | 0.0022505 | 3.436 | 6.9991e-05 | 0.4483 | 9.1319e-06 | 7.9123e-05 | 0.0045451 | 0.000593 | 0.0051381 | 0.022505
Nickel | NA | 0.0021 | NA | 0.0020415 | 0.0020415 | NA | 0.0089417 | 0.0089417 | NA | NA | 15.4334 | 0.00031438 | 0.00031438 | NA | 0.0020415 | 0.0020415 | 0.0089417
Phenanathrene | NA | 1.7e-05 | NA | 1.6526e-06 | 1.6526e-06 | NA | 7.2385e-06 | 7.2385e-06 | NA | NA | 0.012494 | 2.545e-07 | 2.545e-07 | NA | 1.6526e-05 | 1.6526e-05 | 7.2385e-05
POM | 2.2e-06 | NA | 0.00076916 | NA | 0.00076916 | 0.0033689 | NA | 0.0033689 | 5.8148 | 0.00011845 | NA | NA | 0.00011845 | 0.0076916 | NA | 0.0076916 | 0.033689
Pyrene | NA | 5e-06 | NA | 4.8607e-07 | 4.8607e-07 | NA | 2.129e-06 | 2.129e-06 | NA | NA | 0.0036746 | 7.4852e-08 | 7.4852e-08 | NA | 4.8607e-06 | 4.8607e-06 | 2.129e-05
Toluene | 0.00013 | 0.0034 | 0.045451 | 0.00033053 | 0.045781 | 0.19907 | 0.0014477 | 0.20052 | 343.6005 | 0.0069991 | 2.4987 | 5.0899e-05 | 0.00705 | 0.45451 | 0.0033053 | 0.45781 | 2.0052
Xylenes | 6.4e-05 | NA | 0.022376 | NA | 0.022376 | 0.098005 | NA | 0.098005 | 169.1572 | 0.0034457 | NA | NA | 0.0034457 | 0.22376 | NA | 0.22376 | 0.98005
58.3873
NA = No Emission Factor Available.
(1) Combustion Turbine (CT) HAP emission factors obtained from EPA's AP-42 Section 3.1, except formaldehyde, which is based on the EPA 95th upper percentile emission factor for CTGs (EPA August 21, 2001 memorandum). The formaldehyde emission factor of 3.0E-04 was obtained by taking the formaldehyde factor in Table 3 of the 8/21/2001 memo of 2.92E-03 lb/MMBtu and applying a control efficiency of 90% to account for the use of Oxidation Catalysts. This value was rounded to 3.0E-04.
(2) Duct Burner (DB) HAP emission factors obtained from EPA's AP-42 Chapter 1.4, Tables 1.4-3 and 1.4-4.
(3) A control efficiency of 90% was applied to CT & DB organic HAP emissions to account for the use of Oxidation Catalysts, with the exception of the CT formaldehyde emissions, which are calculated using a controlled factor.
Hazardous Air Pollutant (HAP) | One CT (lb/hr) | One DB (lb/hr) | One CT + One DB (lb/hr) | Auxiliary Boiler (lb/hr) | Fuel Gas Heater (lb/hr) | Emergency Generator (lb/hr) | Fire Water Pump (lb/hr) | One CT + One DB (tons/yr) | Auxiliary Boiler (tons/yr) | Fuel Gas Heater (tons/yr) | Emergency Generator (tons/yr) | Fire Water Pump (tons/yr) | Facility Total (tons/yr)
2-Methylnaphthalene | NA | 2.3331e-06 | 2.3331e-06 | 1.8122e-06 | 1.2746e-07 | NA | NA | 1.0219e-05 | 4.1463e-06 | 5.5826e-07 | NA | NA | 1.4924e-05
Acetaldehyde | 0.013985 | NA | 0.013985 | NA | NA | 0.00048686 | 0.0016107 | 0.061253 | NA | NA | 2.4343e-05 | 8.0535e-05 | 0.061358
Acrolein | 0.0022376 | NA | 0.0022376 | NA | NA | 0.00015224 | 0.000788 | 0.0098005 | NA | NA | 7.6121e-06 | 1.182e-06 | 0.0098093
Arsenic | NA | 0.00019443 | 0.00019443 | 1.5102e-05 | 1.0621e-06 | NA | NA | 0.00085159 | 3.4553e-05 | 4.6522e-06 | NA | NA | 0.0008908
Benzene | 0.0041954 | 0.00020415 | 0.0043996 | 0.00015857 | 1.1153e-05 | 0.014992 | 0.0019593 | 0.01927 | 0.0003628 | 4.8848e-05 | 0.00074962 | 9.7965e-05 | 0.020529
Cadmium | NA | 0.0010693 | 0.0010693 | 8.306e-05 | 5.8418e-06 | NA | NA | 0.0046838 | 0.00019004 | 2.5587e-05 | NA | NA | 0.0048994
Chromium | NA | 0.001361 | 0.001361 | 0.00010571 | 7.435e-06 | NA | NA | 0.0059611 | 0.00024187 | 3.2565e-05 | NA | NA | 0.0062356
Cobalt | NA | 8.1659e-05 | 8.1659e-05 | 6.3427e-06 | 4.461e-07 | NA | NA | 0.00035767 | 1.4512e-05 | 1.9539e-06 | NA | NA | 0.00037413
Dichlorobenzene | NA | 0.00011666 | 0.00011666 | 9.061e-05 | 6.3729e-06 | NA | NA | 0.00051095 | 0.00020732 | 2.7913e-05 | NA | NA | 0.00074618
Ethylbenzene | 0.011188 | NA | 0.011188 | NA | NA | NA | NA | 0.049003 | NA | NA | NA | NA | 0.049003
Fluoranthene | NA | 2.9164e-07 | 2.9164e-07 | 2.2653e-07 | 1.5932e-08 | NA | NA | 1.2774e-06 | 5.1829e-07 | 6.9783e-08 | NA | NA | 1.8655e-06
Fluorene | NA | 2.722e-07 | 2.722e-07 | 2.1142e-07 | 1.487e-08 | NA | NA | 1.1922e-06 | 4.8374e-07 | 6.5131e-08 | NA | NA | 1.7411e-06
Formaldehyde | 1.0489 | 0.007291 | 1.0562 | 0.0056632 | 0.00039831 | 0.0015243 | 0.002478 | 4.6259 | 0.012957 | 0.0017446 | 7.6217e-05 | 0.0001239 | 4.6408
Hexane | NA | 0.17498 | 0.17498 | 0.13592 | 0.0095593 | NA | NA | 0.76643 | 0.31098 | 0.04187 | NA | NA | 1.1193
Manganese | NA | 0.00036941 | 0.00036941 | 2.8693e-05 | 2.0181e-06 | NA | NA | 0.001618 | 6.565e-05 | 8.8392e-06 | NA | NA | 0.0016925
Mercury | NA | 0.00025276 | 0.00025276 | 1.9632e-05 | 1.3808e-06 | NA | NA | 0.0011071 | 4.4919e-05 | 6.0479e-06 | NA | NA | 0.001158
Naphthalene | 0.00045451 | 5.93e-05 | 0.00051381 | 4.606e-05 | 3.2395e-06 | 0.0025116 | 0.00017808 | 0.0022505 | 0.00010539 | 1.4189e-05 | 0.00012558 | 8.904e-06 | 0.0025045
Nickel | NA | 0.0020415 | 0.0020415 | 0.00015857 | 1.1153e-05 | NA | NA | 0.0089417 | 0.0003628 | 4.8848e-05 | NA | NA | 0.0093534
Phenanathrene | NA | 1.6526e-06 | 1.6526e-06 | 1.2836e-06 | 9.0283e-08 | NA | NA | 7.2385e-06 | 2.937e-06 | 3.9544e-07 | NA | NA | 1.0571e-05
POM | 0.00076916 | NA | 0.00076916 | NA | NA | 0.0040958 | 0.0003528 | 0.0033689 | NA | NA | 0.00020479 | 1.764e-05 | 0.0035914
Pyrene | NA | 4.8607e-07 | 4.8607e-07 | 3.7754e-07 | 2.6554e-08 | NA | NA | 2.129e-06 | 8.6382e-07 | 1.1631e-07 | NA | NA | 3.1091e-06
Toluene | 0.045451 | 0.00033053 | 0.045781 | 0.00025673 | 1.8057e-05 | 0.0054289 | 0.0008589 | 0.20052 | 0.0005874 | 7.9087e-05 | 0.00027145 | 4.2945e-05 | 0.2015
Xylenes | 0.022376 | NA | 0.022376 | NA | NA | 0.0037288 | 0.0005985 | 0.098005 | NA | NA | 0.00018644 | 2.9925e-05 | 0.098222
Maximum Emissions (Single HAP) | [12 empty] | 4.6408
Total HAPs | [12 empty] | 6.232
NA = No Emission Factor Available.

## Circuit Breakers SF6
ESC Harrison County Power, LLC
Emission Calculations - GHGs (SF6) from Circuit Breakers
Pollutant | Emission Source | Count (Breakers) | Mass of SF6 per Breaker (lb/Breaker/year) | Annual SF6 Leak Rate (% by weight) | SF6 Mass Emissions (tons/yr) | Global Warming Potential | CO2e (tons/yr)
SF6 | Generator Breakers | 2 | 25 | 0.5% | 0.000125 | 22800 | 2.85
SF6 | Switchyard Circuit Breakers | 3 | 325 | 0.5% | 0.0024375 | 22800 | 55.575
Total |  | 5 | 350 |  | 0.0025625 |  | 58.425
(1)The annual mass emissions of SF6 from electrical breakers are calculated using the number of breakers, mass of SF6 per breaker, and annual leak rate as follows:
SF6 for Breakers (tons/yr) = Number of Breakers x Mass of SF6 per Breaker (lb) x Annual SF6 Leak Rate (%) x 1 ton/2000 lb
(2) The Global Warming Potential factor for SF6 was obtained from 40 CFR Part 98, Subpart A, Table A-1.

## HARRISON T218 REV D 10042016
Combined Cycle Systems Emissions Estimates
OPERATING POINT |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | MIN | AVG | MAX
Case Description |  | 100% DB Firing | 10% DB Firing | Unfired | Unfired | Unfired | 94% DB Firing | 10% DB Firing | Unfired | Unfired | Unfired | 88% DB Firing | 10% DB Firing | Unfired | Unfired | Unfired | 80% DB Firing | Unfired | 10% DB Firing | Unfired | Unfired | Unfired | 91% DB Firing | 10% DB Firing | Unfired | Unfired | Unfired | Unfired
SITE CONDITIONS
Ambient Temperature | °F | -12.2 | -12.2 | -12.2 | -12.2 | -12.2 | 32 | 32 | 32 | 32 | 32 | 53.6 | 53 | 53.6 | 53.6 | 53.6 | 87.6 | 87.6 | 87.6 | 87.6 | 87.6 | 87.6 | 99 | 99 | 99 | 99 | 99 | 99 | -12.2 | 55.037 | 99
Ambient Pressure | psia | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14
Ambient Relative Humidity | % | 80 | 80 | 80 | 80 | 80 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 45.9 | 45.9 | 45.9 | 45.9 | 45.9 | 45.9 | 31.8 | 31.8 | 31.8 | 31.8 | 31.8 | 31.8 | 31.8 | 54.3037 | 80
PLANT STATUS
HRSG Duct Burner |  | Fired | Fired | Unfired | Unfired | Unfired | Fired | Fired | Unfired | Unfired | Unfired | Fired | Fired | Unfired | Unfired | Unfired | Fired | Unfired | Fired | Unfired | Unfired | Unfired | Fired | Fired | Unfired | Unfired | Unfired | Unfired
SCR |  | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating
CO Catalyst |  | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating
Evaporative Cooler Status |  | off | off | off | off | off | off | off | off | off | off | off | off | off | off | off | on | on | off | off | off | off | on | off | on | off | off | off
Net Equipment Combined Cycle Load | % | BASE | BASE | BASE | 75% | MECL | BASE | BASE | BASE | 75% | MECL | BASE | BASE | BASE | 75% | MECL | BASE | BASE | BASE | BASE | 75% | MECL | BASE | BASE | BASE | BASE | 75% | MECL
Gas Turbines Operating |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
GT Diluent Injection Type |  | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
GT Diluent Injection Flow (per GT) | 10^3 lb/hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FUEL DATA
Fuel Type |  | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG
HHV | Btu/lb | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872 | 23482.1872
LHV | Btu/lb | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219 | 21185.2219
Fuel Mol. Wt. | lb/mole | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437 | 16.9437
Fuel Bound Nitrogen | Wt % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fuel Sulfur Content | grains/100 SCF @ 60°F | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
GT Heat Consumption per unit with Permitting Margin See HRSG NOTE 10 | MMBtu/hr, HHV | 3496.2 | 3495.1 | 3495.7 | 2672.9 | 1985.2 | 3480.2 | 3480 | 3480.4 | 2597.8 | 1541.2 | 3427.6 | 3432 | 3428 | 2612.6 | 1505.9 | 3306.1 | 3306.5 | 3166.5 | 3167.1 | 2434.6 | 1569 | 3278.4 | 3031.5 | 3278.8 | 3032.1 | 2341.2 | 1581 | 1505.9 | 2874.9481 | 3496.2
Duct Burner Heat Consumption | MMBtu/hr, HHV | 1001.3 | 99.247 | 3.7821e-13 | 3.7821e-13 | 3.7821e-13 | 940.41 | 99.247 | 3.7821e-13 | 3.7821e-13 | 3.7821e-13 | 877.39 | 99.247 | 3.7821e-13 | 3.7821e-13 | 3.7821e-13 | 803.21 | 3.7821e-13 | 99.247 | 3.7821e-13 | 3.7821e-13 | 3.7821e-13 | 913.67 | 99.247 | 3.7821e-13 | 3.7821e-13 | 3.7821e-13 | 3.7821e-13 | 3.7821e-13 | 186.3783 | 1001.3
HRSG DATA (PER UNIT)
HRSG EXIT EXHAUST GAS
Composition:
Ar | mol % | 0.8792 | 0.88911 | 0.8902 | 0.89057 | 0.89585 | 0.87654 | 0.88587 | 0.88698 | 0.88747 | 0.8924 | 0.87281 | 0.88168 | 0.88265 | 0.88294 | 0.88841 | 0.85829 | 0.8674 | 0.87117 | 0.87235 | 0.87324 | 0.87776 | 0.855 | 0.87159 | 0.8654 | 0.87282 | 0.87416 | 0.87815 | 0.855 | 0.87852 | 0.89585
CO2 | mol % | 5.4977 | 4.4241 | 4.3055 | 4.2658 | 3.6906 | 5.4794 | 4.4656 | 4.3444 | 4.2909 | 3.7525 | 5.419 | 4.4678 | 4.3437 | 4.3122 | 3.7126 | 5.325 | 4.311 | 4.3932 | 4.2628 | 4.1639 | 3.6615 | 5.4633 | 4.3759 | 4.3035 | 4.2407 | 4.0911 | 3.648 | 3.648 | 4.4078 | 5.4977
H2O | mol % | 10.7808 | 8.6894 | 8.4582 | 8.3803 | 7.2497 | 11.0502 | 9.0787 | 8.8429 | 8.7379 | 7.6813 | 11.3937 | 9.5305 | 9.3075 | 9.246 | 8.0722 | 12.8654 | 10.9159 | 10.5882 | 10.3367 | 10.1444 | 9.1669 | 13.3509 | 10.5258 | 11.1239 | 10.2651 | 9.9742 | 9.112 | 7.2497 | 9.8099 | 13.3509
N2 | mol % | 73.8502 | 74.6697 | 74.7603 | 74.7908 | 75.233 | 73.6263 | 74.3976 | 74.4899 | 74.5308 | 74.9434 | 73.3124 | 74.0466 | 74.1265 | 74.1505 | 74.6078 | 72.092 | 72.8459 | 73.1637 | 73.2612 | 73.3356 | 73.714 | 71.8176 | 73.199 | 72.6779 | 73.3001 | 73.4128 | 73.7466 | 71.8176 | 73.7816 | 75.233
O2 | mol % | 8.9921 | 11.3276 | 11.5858 | 11.6725 | 12.9308 | 8.9676 | 11.1722 | 11.4359 | 11.5529 | 12.7303 | 9.002 | 11.0735 | 11.3396 | 11.4083 | 12.719 | 8.8594 | 11.0598 | 10.9838 | 11.267 | 11.4828 | 12.5798 | 8.5132 | 11.0277 | 11.0293 | 11.3213 | 11.6478 | 12.6152 | 8.5132 | 11.1221 | 12.9308
O2, dry basis | mol % | 10.0787 | 12.4056 | 12.6563 | 12.7402 | 13.9415 | 10.0816 | 12.2878 | 12.5453 | 12.659 | 13.7895 | 10.1596 | 12.24 | 12.5034 | 12.5706 | 13.8358 | 10.1675 | 12.415 | 12.2845 | 12.5659 | 12.7792 | 13.8494 | 9.8249 | 12.325 | 12.4097 | 12.6164 | 12.9383 | 13.88 | 9.8249 | 12.3167 | 13.9415
Molecular weight |  | 28.2785 | 28.4102 | 28.4247 | 28.4297 | 28.5015 | 28.2474 | 28.3713 | 28.3861 | 28.3928 | 28.4598 | 28.2043 | 28.322 | 28.3352 | 28.3391 | 28.4134 | 28.0347 | 28.1562 | 28.1995 | 28.2152 | 28.2274 | 28.289 | 27.9941 | 28.2048 | 28.1328 | 28.2211 | 28.2394 | 28.2938 | 27.9941 | 28.2861 | 28.5015
Temperature | °F | 136.0398 | 170.9034 | 175.9407 | 168.0367 | 173.833 | 141.383 | 167.8999 | 172.6238 | 164.5623 | 158.2849 | 153.6717 | 167.7142 | 171.0563 | 162.7537 | 157.9661 | 174.1475 | 186.0931 | 181.1933 | 184.0447 | 173.5246 | 167.376 | 183.9745 | 186.9698 | 193.4567 | 189.3399 | 180.6039 | 175.2436 | 136.0398 | 171.0606 | 193.4567
Mass Flow with Permitting Margin See HRSG NOTE 10 | lb/hr | 6173900 | 6133700 | 6129200 | 4731200 | 4076300 | 6080900 | 6043300 | 6038900 | 4565100 | 3107300 | 5977400 | 5948800 | 5938200 | 4559500 | 3063900 | 5770100 | 5734200 | 5571000 | 5566600 | 4383500 | 3222700 | 5731900 | 5362600 | 5691100 | 5358200 | 4292700 | 3260000 | 3063900 | 5130081.4815 | 6173900
Mole flow actual | lb-mole/hr | 218324.6081 | 215898.1284 | 215629.3004 | 166417.7652 | 143020.7237 | 215273.171 | 213007.5322 | 212741.2895 | 160783.8429 | 109182.0568 | 211932.2152 | 210041.3369 | 209569.7569 | 160890.8302 | 107832.8448 | 205819.9107 | 203656.7631 | 197556.3961 | 197290.4981 | 155292.5477 | 113920.6861 | 204753.8823 | 190130.7494 | 202294.3776 | 189865.1528 | 152010.8982 | 115219.6968 | 107832.8448 | 181420.6282 | 218324.6081
Mole flow dry | lb-mole/hr, dry | 194787.5533 | 197137.8825 | 197390.9571 | 152471.4952 | 132652.1808 | 191484.9718 | 193669.2745 | 193928.8938 | 146734.6943 | 100795.4095 | 187785.2663 | 190023.4022 | 190063.9984 | 146014.8724 | 99128.3454 | 179340.3629 | 181425.7122 | 176638.8224 | 176897.2266 | 139539.1174 | 103477.6577 | 177417.3906 | 170117.9649 | 179791.3851 | 170375.2903 | 136849.0696 | 104720.8523 | 99128.3454 | 163357.7796 | 197390.9571
Mole flow dry at 15% O2 | lb-mole/hr, dry @ 15% O2 | 357264.9132 | 283825.6215 | 275801.6546 | 210870.8672 | 156451.0713 | 351111.9703 | 282697.7817 | 274613.0385 | 204955.5962 | 121475.3486 | 341845.4893 | 278915.8452 | 270490.9003 | 206138.3244 | 118688.2927 | 326232.9264 | 260915.7665 | 257938.9831 | 249877.8744 | 192062.4206 | 123658.0484 | 333036.1238 | 247247.4613 | 258724.4041 | 239207.6189 | 184670.8039 | 124600.209 | 118688.2927 | 241974.7909 | 357264.9132
Actual Volume Flow | Actual ft3/hr | 98710000 | 103320000 | 104020000 | 79282000 | 68766000 | 98203000 | 101460000 | 102090000 | 76175000 | 51207000 | 98655000 | 100010000 | 100320000 | 76005000 | 50548000 | 99009000 | 99815000 | 96089000 | 96387000 | 74630000 | 54216000 | 100020000 | 93312000 | 100280000 | 93522000 | 73869000 | 55522000 | 50548000 | 86868222.2222 | 104020000
Actual Volume Flow | Actual ft3/min | 1645166.6667 | 1722000 | 1733666.6667 | 1321366.6667 | 1146100 | 1636716.6667 | 1691000 | 1701500 | 1269583.3333 | 853450 | 1644250 | 1666833.3333 | 1672000 | 1266750 | 842466.6667 | 1650150 | 1663583.3333 | 1601483.3333 | 1606450 | 1243833.3333 | 903600 | 1667000 | 1555200 | 1671333.3333 | 1558700 | 1231150 | 925366.6667 | 842466.6667 | 1447803.7037 | 1733666.6667
HRSG EXIT EXHAUST GAS EMISSIONS
NOx | ppmvd @ 15% O2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
NOx | lb/hr as NO2 | 32.9 | 26.1 | 25.4 | 19.4 | 14.4 | 32.3 | 26 | 25.3 | 18.9 | 11.2 | 31.4 | 25.7 | 24.9 | 19 | 10.9 | 30 | 24 | 23.7 | 23 | 17.7 | 11.4 | 30.6 | 22.7 | 23.8 | 22 | 17 | 11.5 | 10.9 | 22.2667 | 32.9
CO | ppmvd @ 15% O2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
CO | lb/hr | 20 | 15.9 | 15.4 | 11.8 | 8.76 | 19.7 | 15.8 | 15.4 | 11.5 | 6.8 | 19.1 | 15.6 | 15.1 | 11.5 | 6.65 | 18.3 | 14.6 | 14.4 | 14 | 10.8 | 6.92 | 18.7 | 13.8 | 14.5 | 13.4 | 10.3 | 6.98 | 6.65 | 13.5448 | 20
VOC | ppmvd @ 15% O2 | 2 | 2 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 2 | 1 | 2 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1.3704 | 2
VOC | lb/hr as methane | 11.4 | 9.08 | 4.41 | 3.37 | 2.5 | 11.2 | 9.05 | 4.39 | 3.28 | 1.94 | 10.9 | 8.93 | 4.33 | 3.3 | 1.9 | 10.4 | 4.17 | 8.25 | 4 | 3.07 | 1.98 | 10.7 | 7.91 | 4.14 | 3.83 | 2.95 | 1.99 | 1.9 | 5.6804 | 11.4
CO2 | lb/hr | 528000 | 420000 | 409000 | 312000 | 232000 | 519000 | 419000 | 407000 | 304000 | 180000 | 505000 | 413000 | 401000 | 305000 | 176000 | 482000 | 386000 | 382000 | 370000 | 285000 | 184000 | 492000 | 366000 | 383000 | 354000 | 274000 | 185000 | 176000 | 358259.2593 | 528000
CH4 | lb/hr | 9.9153 | 7.9242 | 7.7067 | 5.8927 | 4.3766 | 9.7458 | 7.8909 | 7.673 | 5.7272 | 3.3978 | 9.4909 | 7.7851 | 7.5574 | 5.7598 | 3.3199 | 9.0595 | 7.2896 | 7.1997 | 6.9823 | 5.3674 | 3.459 | 9.2419 | 6.9021 | 7.2285 | 6.6846 | 5.1615 | 3.4855 | 3.3199 | 6.7491 | 9.9153
N2O | lb/hr | 0.99153 | 0.79242 | 0.77067 | 0.58927 | 0.43766 | 0.97458 | 0.78909 | 0.7673 | 0.57272 | 0.33978 | 0.94909 | 0.77851 | 0.75574 | 0.57598 | 0.33199 | 0.90595 | 0.72896 | 0.71997 | 0.69823 | 0.53674 | 0.3459 | 0.92419 | 0.69021 | 0.72285 | 0.66846 | 0.51615 | 0.34855 | 0.33199 | 0.67491 | 0.99153
GHG (Mass Basis) | lb/hr | 528010.9068 | 420008.7166 | 409008.4774 | 312006.482 | 232004.8143 | 519010.7203 | 419008.68 | 407008.4403 | 304006.2999 | 180003.7375 | 505010.44 | 413008.5636 | 401008.3132 | 305006.3358 | 176003.6519 | 482009.9654 | 386008.0185 | 382007.9197 | 370007.6805 | 285005.9041 | 184003.805 | 492010.1661 | 366007.5923 | 383007.9514 | 354007.3531 | 274005.6776 | 185003.8341 | 176003.6519 | 358266.6832 | 528010.9068
GHG (CO2e Basis) | lb/hr | 528543.3573 | 420434.2445 | 409422.3266 | 312322.9215 | 232239.8383 | 519534.0679 | 419432.4202 | 407420.4782 | 304313.8485 | 180186.1973 | 505520.0995 | 413426.6212 | 401414.1476 | 305315.6365 | 176181.9326 | 482496.4588 | 386399.4688 | 382394.5453 | 370382.6274 | 285294.1318 | 184189.5559 | 492506.4573 | 366378.2355 | 383396.1222 | 354366.3176 | 274282.8478 | 185191.0056 | 176181.9326 | 358629.1078 | 528543.3573
NH3 | ppmvd @ 15% O2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
NH3 | lb/hr | 30.4 | 24.1 | 23.4 | 17.9 | 13.3 | 29.8 | 24 | 23.3 | 17.4 | 10.3 | 29.1 | 23.7 | 23 | 17.5 | 10.1 | 27.7 | 22.2 | 21.9 | 21.2 | 16.3 | 10.5 | 28.3 | 21 | 22 | 20.3 | 15.7 | 10.6 | 10.1 | 20.5556 | 30.4
SOx @ 0.5 gr/100 scf | lb/hr as SO2 | 7.44 | 5.88 | 5.712 | 4.368 | 3.24 | 7.308 | 5.856 | 5.688 | 4.248 | 2.52 | 7.116 | 5.784 | 5.604 | 4.272 | 2.46 | 6.78 | 5.412 | 5.352 | 5.184 | 3.984 | 2.568 | 6.924 | 5.124 | 5.364 | 4.956 | 3.828 | 2.58 | 2.46 | 5.0204 | 7.44
SOx @ 0.4 gr/100 scf | lb/hr as SO2 | 5.952 | 4.704 | 4.5696 | 3.4944 | 2.592 | 5.8464 | 4.6848 | 4.5504 | 3.3984 | 2.016 | 5.6928 | 4.6272 | 4.4832 | 3.4176 | 1.968 | 5.424 | 4.3296 | 4.2816 | 4.1472 | 3.1872 | 2.0544 | 5.5392 | 4.0992 | 4.2912 | 3.9648 | 3.0624 | 2.064 | 1.968 | 4.0164 | 5.952
SOx @ 0.5 gr/100 scf | lb/MMBtu | 0.0016543 | 0.0016359 | 0.001634 | 0.0016342 | 0.0016321 | 0.0016532 | 0.0016361 | 0.0016343 | 0.0016352 | 0.0016351 | 0.001653 | 0.0016379 | 0.0016348 | 0.0016352 | 0.0016336 | 0.0016499 | 0.0016368 | 0.0016388 | 0.0016368 | 0.0016364 | 0.0016367 | 0.0016517 | 0.0016367 | 0.001636 | 0.0016345 | 0.0016351 | 0.0016319 | 0.0016319 | 0.0016385 | 0.0016543
SOx @ 0.4 gr/100 scf | lb/MMBtu | 0.0013234 | 0.0013087 | 0.0013072 | 0.0013073 | 0.0013057 | 0.0013225 | 0.0013089 | 0.0013074 | 0.0013082 | 0.0013081 | 0.0013224 | 0.0013104 | 0.0013078 | 0.0013081 | 0.0013069 | 0.0013199 | 0.0013094 | 0.0013111 | 0.0013095 | 0.0013091 | 0.0013094 | 0.0013214 | 0.0013093 | 0.0013088 | 0.0013076 | 0.001308 | 0.0013055 | 0.0013055 | 0.0013108 | 0.0013234
Particulates F+C, Including Sulfates | lb/hr | 22.6 | 21.6 | 11.6 | 10.9 | 10.3 | 21.9 | 21.6 | 11.6 | 10.8 | 10 | 21.2 | 21.5 | 11.5 | 10.8 | 9.9 | 20.3 | 11.4 | 21.3 | 11.3 | 10.7 | 10 | 21.5 | 21.2 | 11.4 | 11.2 | 10.6 | 10 | 9.9 | 14.7667 | 22.6
Particulates F+C, Including Sulfates | lb/MMBtu | 0.005025 | 0.0060094 | 0.0033184 | 0.004078 | 0.0051884 | 0.0049541 | 0.0060348 | 0.003333 | 0.0041574 | 0.0064885 | 0.0049245 | 0.0060885 | 0.0033547 | 0.0041338 | 0.0065741 | 0.00494 | 0.0034478 | 0.0065222 | 0.0035679 | 0.004395 | 0.0063735 | 0.0051287 | 0.0067715 | 0.0034769 | 0.0036938 | 0.0045276 | 0.0063251 | 0.0033184 | 0.0049197 | 0.0067715
Sulfuric Acid Mist @ 0.5 gr/100 scf | lb/hr | 4.78 | 3.78 | 3.67 | 2.81 | 2.09 | 4.69 | 3.77 | 3.66 | 2.73 | 1.62 | 4.57 | 3.71 | 3.6 | 2.74 | 1.58 | 4.36 | 3.47 | 3.44 | 3.33 | 2.56 | 1.65 | 4.45 | 3.29 | 3.44 | 3.19 | 2.46 | 1.66 | 1.58 | 3.2259 | 4.78
Sulfuric Acid Mist @ 0.4 gr/100 scf | lb/hr | 3.824 | 3.024 | 2.936 | 2.248 | 1.672 | 3.752 | 3.016 | 2.928 | 2.184 | 1.296 | 3.656 | 2.968 | 2.88 | 2.192 | 1.264 | 3.488 | 2.776 | 2.752 | 2.664 | 2.048 | 1.32 | 3.56 | 2.632 | 2.752 | 2.552 | 1.968 | 1.328 | 1.264 | 2.5807 | 3.824
Sulfuric Acid Mist @ 0.5 gr/100 scf | lb/MMBtu | 0.0010628 | 0.0010517 | 0.0010499 | 0.0010513 | 0.0010528 | 0.0010609 | 0.0010533 | 0.0010516 | 0.0010509 | 0.0010511 | 0.0010616 | 0.0010506 | 0.0010502 | 0.0010488 | 0.0010492 | 0.001061 | 0.0010494 | 0.0010534 | 0.0010514 | 0.0010515 | 0.0010516 | 0.0010615 | 0.0010509 | 0.0010492 | 0.0010521 | 0.0010507 | 0.00105 | 0.0010488 | 0.0010529 | 0.0010628
Sulfuric Acid Mist @ 0.4 gr/100 scf | lb/MMBtu | 0.00085025 | 0.00084132 | 0.00083989 | 0.00084103 | 0.00084223 | 0.00084875 | 0.00084264 | 0.00084128 | 0.00084071 | 0.0008409 | 0.00084925 | 0.0008405 | 0.00084014 | 0.00083901 | 0.00083937 | 0.0008488 | 0.00083956 | 0.00084269 | 0.00084115 | 0.00084121 | 0.0008413 | 0.00084922 | 0.00084069 | 0.00083933 | 0.00084166 | 0.00084059 | 0.00083997 | 0.00083901 | 0.00084235 | 0.00085025
The notes page is an integral part of this document and must be reviewed prior to use of this data.
Worst Case Operating Parameters |  |  | Operating Point(s)
GT Heat Consumption per unit with Permitting Margin See HRSG NOTE 10 | MMBtu/hr, HHV | 3496.2 | 1
Duct Burner Heat Consumption | MMBtu/hr, HHV | 1001.3 | 1
Total Heat Consumption (CT+DB) | MMBtu/hr, HHV | 4497.5 | 1
Worst Case Emission Rates |  |  | Operating Point(s)
NOx | lb/hr | 32.9 | 1
CO | lb/hr | 20 | 1
VOC | lb/hr | 11.4 | 1
SO2 @ 0.4 gr/100 scf | lb/hr | 5.952 | 1
PM/PM10/PM2.5 | lb/hr | 22.6 | 1
H2SO4 @ 0.4 gr/100 scf | lb/hr | 3.824 | 1
CO2 | lb/hr | 528000 | 1
CH4 | lb/hr | 9.9153 | 1
N2O | lb/hr | 0.99153 | 1
GHG (Mass Basis) | lb/hr | 528010.9068 | 1
GHG (CO2e Basis) | lb/hr | 528543.3573 | 1
SO2 @ 0.4 gr/100 scf | lb/MMBtu | 0.0013234 | Various
PM/PM10/PM2.5 | lb/MMBtu | 0.0067715 | 23
H2SO4 @ 0.4 gr/100 scf | lb/MMBtu | 0.00085025 | 1
T218 Fuel Sulfur Content | (gr/100 scf) | 0.5
Proposed Fuel Sulfur Content | (gr/100 scf) | 0.4
HHV - Natural Gas | Btu/lb | 23482.1872
LHV - Natural Gas | Btu/lb | 21185.2219
Conversion Factor (kg to lb) | 2.2046
CO2 Emission Factor (kg/MMBtu) | 53.02
CO2 Emission Factor (lb/MMBtu) | 116.889
CH4 Emission Factor (kg/MMBtu) | 0.001
CH4 Emission Factor (lb/MMBtu) | 0.0022046
N2O Emission Factor (kg/MMBtu) | 0.0001
N2O Emission Factor (lb/MMBtu) | 0.00022046
Global Warming Potential - CO2 | 1
Global Warming Potential - CH4 | 25
Global Warming Potential - N2O | 298

## HARRISON Cus Notes REV D
Estimated Steady State Emission Notes
HRSG Emission Notes:
1. Gas turbine(s) and steam plant are in steady-state operation.
2. HRSG Stack Exhaust emissions are reported based on the following conversion rates:
- Gas Turbine: 95% conversion of sulfur to SO2 and 5% conversion to SO3.
- Duct Burner: 95% conversion of sulfur to SO2 and 5% conversion to SO3.
- For installations that are equipped with a CO catalyst it is expected that 10% to about 35% of the SO2 in
the exhaust gas is converted to SO3. The actual conversion rate used in these calculations is 30%.
- For installations with an SCR catalyst for NOx abatement it is expected that 1% to 5% of the SO2 in the
exhaust gas will be converted to SO3. The actual conversion rate used in these calculations is 5%.
3. HRSG Stack NH3 Emissions are based on assuming no conversion to ammonium salts
4. Steady State Emissions data above are estimated values based on GE recommended
measurements and analysis procedures, per GEK 28172.
5. Reference conditions for exhaust gas SCF are: 68°F, and 14.6959 psia.
Reference conditions for exhaust gas fuel SCF are: 60°F, and 14.6959 psia.
6. Reference conditions for exhaust gas Nm3 are: 32°F, and 14.6959 psia.
Reference conditions for gas fuel Nm3 are: 60°F, and 14.6959 psia.
7. SO2 emission values have been estimated by assuming that all the sulfur in the fuel is converted to
SO2 and is based on maximum S content in the fuel of 0.5 grains/100 SCF @ 60°F for gas.
SO2 values are margined by 20% to account for variation in fuel sulfur content and
measurement error.
8. The CO2 estimate derived from the heat rate does not include any margin for measurement errors
assuming that the compliance will be demonstrated using the heat rate from the performance test
results. If CO2 compliance is to be demonstrated using actual CO2 measurements from the HRSG stack,
GE recommends adding 10% margin to the estimated values.
9. Sulfur mist emission calculations conservatively assume that all SO3 combines with water to form
sulfur mist. In actuality, some SO3 may form other chemical species. This would include ammonium
sulfates in the presence of NH3. The maximum sulfur mist is reported to be conservative.
10. The estimated values for heat consumption and the exhaust flows are margined in this document
to account for equipment variations, site operating conditions and life-cycle operating parameters.
The Plant Performance section does not include permitting margin, for more information on
performance please refer to the Heat Balance.
Additional Notes for Particulate Emissions
1. Particulate Matter estimates over the entire emissions compliance region of GT operation are
based on field data obtained at base load for the GT. In reality, particulate matter emissions
measured in lb/h are expected to decrease at part load operation and the lb/MMBTU values at
part load operation are expected not to exceed the lb/MMBTU value for PM at baseload.
2. PM10 and PM2.5 are estimated at the same rate as Total Particulates.
3. PM estimates are based on maximum S content in the fuel of 0.5 grains/100 SCF @ 60°F for gas.

## Stack Parameters
Combustion Turbine/Duct Burners
Exhaust Flow | 1733666.6667 | acfm | Maximum flow rate, based on -12.2°F, 0% DF, evap cooling off, and base load (Operating Point 3).
Stack Diameter | 21.5 | ft.
Exit Velocity | 79.588 | ft/sec
Stack Height | 205 | ft.
Exit Temp. | 136.0398 | °F | Minimum stack temperature, based on -12.2°F, 100% DF, evap cooling off, and base load (Operating Point 1).
Auxiliary Boiler
Exhaust Flow | 13846 | acfm
Stack Diameter | 27 | in.
Stack Diameter | 2.25 | ft.
Exit Velocity | 58.0388 | ft/sec
Stack Height | 35 | ft.
Exit Temp. | 399.8167 | K
Exit Temp. | 260 | °F
Fuel Gas Heater
Exhaust Flow | 973 | acfm
Stack Diameter | 7 | in.
Stack Diameter | 0.58333 | ft.
Exit Velocity | 60.679 | ft/sec
Stack Height | 15 | ft.
Exit Temp. | 588.7056 | K
Exit Temp. | 600 | °F
Emergency Generator
| Stack 1 | Stack 2
Exhaust Flow (total) | 15295 |  | acfm
Exhaust Flow (per stack) | 7647.5 | 7647.5 | acfm
Stack Diameter | 8 | 8 | in
Stack Diameter | 0.66667 | 0.66667 | ft.
Exit Velocity | 111.295 | 111.295 | m/s
Exit Velocity | 365.1412 | 365.1412 | ft/sec
Stack Height | 4.572 | 4.572 | m
Stack Height | 15 | 15 | ft.
Exit Temp. | 673.15 | 673.15 | K
Exit Temp. | 752 | 752 | °F
Fire Water Pump
Exhaust Flow | 1400 | acfm
Stack Diameter | 6 | in
Stack Diameter | 0.5 | ft.
Exit Velocity | 118.8357 | ft/sec
Stack Height | 4.572 | m
Stack Height | 15 | ft.
Exit Temp. | 789.2611 | K
Exit Temp. | 961 | °F