## RevI_Facility Summary
ESC Brooke County Power I, LLC
Facility Emissions Summary Tables
Combined Cycle Units
Pollutant | Maximum Short Term Emissions: 1 CT/DB | Maximum Annual Steady State Emissions: 2 CTs/DBs | Startup and Shutdown Emissions: 2 CTs/DBs | Total Annual Emissions: 2 CTs/DBs
| (lb/ hr ) | (tons/yr) | (tons/yr) | (tons/yr)
VOC | 8.1 | 69.6681 | 15.348 | 85.0161
NOx | 23.2 | 199.5432 | 27.34 | 226.8832
CO | 14.1 | 121.2741 | 122.38 | 243.6541
SO2 | 4 | 35.04 | -- (1) | 35.04
PM10/PM2.5 | 16.9 | 145.3569 | 1.8808 | 147.2377
PM | 16.9 | 145.3569 | 1.8808 | 147.2377
Pb | 0.001329 | 0.011642 | -- (1) | 0.011642
H2SO4 | 2.6 | 22.776 | -- (1) | 22.776
(1)Worst-case annual emissions are addressed by steady-state operation.
Auxiliary Boiler
Pollutant | Maximum Short Term Emissions | Maximum Annual Emissions
| (lb/ hr ) | (tons/yr)
VOC | 0.89535 | 2.0486
NOx | 1.2311 | 2.8168
CO | 4.141 | 9.4746
SO2 | 0.14502 | 0.3318
PM10/PM2.5 | 0.87007 | 1.9907
PM | 0.87007 | 1.9907
Pb | 5.433e-05 | 0.00012431
H2SO4 | 0.011103 | 0.025404
ESC Brooke County Power I, LLC
Facility Emissions Summary Tables
Emergency Generator and Fire Water Pump
Pollutant | Emergency Generator Maximum Short Term Emissions | Emergency Generator Maximum Annual Emissions | Fire Water Pump Maximum Short Term Emissions | Fire Water Pump Maximum Annual Emissions
| (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr)
VOC | 0.65041 | 0.032521 | 0.05764 | 0.002882
NOx | 32.2249 | 1.6112 | 1.8681 | 0.093405
CO | 1.7738 | 0.088692 | 0.30556 | 0.015278
SO2 | 0.029187 | 0.0014594 | 0.0031725 | 0.00015862
PM10/PM2.5 | 0.14782 | 0.007391 | 0.051737 | 0.0025869
PM | 0.14782 | 0.007391 | 0.051737 | 0.0025869
Pb | -- | -- | -- | --
H2SO4 | 0.0044693 | 0.00022346 | 0.00048579 | 7.2868e-07
Fuel Gas Heaters
Pollutant | Fuel Gas Heater Maximum Short Term Emissions (1 FGH) | Fuel Gas Heater Maximum Annual Emissions (1 FGH) | Fuel Gas Heater 2 Maximum Short Term Emissions (2 FGHs)
| (lb/hr) | (tons/yr) | (tons/yr)
VOC | 0.037788 | 0.16551 | 0.33102
NOx | 0.19434 | 0.85119 | 1.7024
CO | 0.20945 | 0.9174 | 1.8348
SO2 | 0.0069948 | 0.030637 | 0.061274
PM10/PM2.5 | 0.041967 | 0.18381 | 0.36763
PM | 0.041967 | 0.18381 | 0.36763
Pb | 2.6205e-06 | 1.1478e-05 | 2.2956e-05
H2SO4 | 0.00053554 | 0.0023457 | 0.0046913
ESC Brooke County Power I, LLC
Facility Emissions Summary Tables
Facility-Wide Emissions Summary
Annual Emissions (tons/yr)
Unit | VOC | NOx | CO | SO2 | PM10 | PM | PM2.5 | Pb | H2SO4 | CO2e
CTs/DBs (2) - Steady State | 69.6681 | 199.5432 | 121.2741 | 35.04 | 145.3569 | 145.3569 | 145.3569 | 0.011642 | 22.776 | 3656265.2545
CTs - Startups & Shutdowns | 15.348 | 27.34 | 122.38 | -- | 1.8808 | 1.8808 | 1.8808 | -- (1) | -- (1) | --
Auxiliary Boiler | 2.0486 | 2.8168 | 9.4746 | 0.3318 | 1.9907 | 1.9907 | 1.9907 | 0.00012431 | 0.025404 | 33789.7065
Fuel Gas Heaters (2) | 0.33102 | 1.7024 | 1.8348 | 0.061274 | 0.36763 | 0.36763 | 0.36763 | 2.2956e-05 | 0.0046913 | 6239.9479
Emergency Generator | 0.032521 | 1.6112 | 0.088692 | 0.0014594 | 0.007391 | 0.007391 | 0.007391 | -- | 0.00022346 | 158.0504
Fire Water Pump | 0.002882 | 0.093405 | 0.015278 | 0.00015862 | 0.0025869 | 0.0025869 | 0.0025869 | -- | 7.2868e-07 | 17.1794
Circuit Breakers | -- | -- | -- | -- | -- | -- | -- | -- | -- | 58.425
Total | 87.4311 | 233.107 | 255.0675 | 35.4347 | 149.606 | 149.606 | 149.606 | 0.011789 | 22.8063 | 3696528.5637
Emission Calculations - GHGs
| CO2 |  | CH4 |  | N2O |  | SF6 |  | CO2e
Source | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr) | (lb/hr) | (tons/yr)
CTs/DBs (2) - Steady State | 834000 | 3652920 | 13.9372 | 61.0448 | 1.3937 | 6.1045 | -- | -- | 834763.7567 | 3656265.2545
Auxiliary Boiler | 14705.6062 | 33646.4269 | 0.74022 | 1.6936 | 0.14804 | 0.33872 | -- | -- | 14768.2284 | 33789.7065
Fuel Gas Heaters (2) | 1418.6047 | 6213.4884 | 0.071406 | 0.31276 | 0.014281 | 0.062552 | -- | -- | 1424.6456 | 6239.9479
Emergency Generator | 3150.1974 | 157.5099 | 0.12778 | 0.006389 | 0.025556 | 0.0012778 | -- | -- | 3161.0076 | 158.0504
Fire Water Pump | 342.4128 | 17.1206 | 0.013889 | 0.00069446 | 0.0027778 | 0.00013889 | -- | -- | 343.5878 | 17.1794
Circuit Breakers | -- | -- | -- | -- | -- | -- | 0.00058505 | 0.0025625 | 13.339 | 58.425
Total CO2e | 853616.821 | 3692954.5459 | 14.8905 | 63.0582 | 1.5844 | 6.5072 | 0.00058505 | 0.0025625 | 854474.5651 | 3696528.5637
ESC Brooke County Power I, LLC
Facility Emissions Summary Tables
Hazardous Air Pollutant (HAP) | Two CT + Two DB (tons/yr) | Auxiliary Boiler (tons/yr) | Fuel Gas Heater (tons/yr) | Emergency Generator (tons/yr) | Fire Water Pump (tons/yr) | Facility Total (tons/yr)
2-Methylnaphthalene | 8.6566e-06 | 5.9667e-06 | 1.1019e-06 | NA | NA | 1.5725e-05
Acetaldehyde | 0.095929 | NA | NA | 2.4343e-05 | 8.0535e-05 | 0.096034
Acrolein | 0.015349 | NA | NA | 7.6121e-06 | 1.182e-06 | 0.015357
Arsenic | 0.00072138 | 4.9722e-05 | 9.1822e-06 | NA | NA | 0.00078029
Benzene | 0.029536 | 0.00052208 | 9.6413e-05 | 0.00074962 | 9.7965e-05 | 0.031002
Cadmium | 0.0039676 | NA | NA | NA | NA | 0.0039676
Chromium | 0.0050497 | 0.00034806 | 6.4276e-05 | NA | NA | 0.005462
Cobalt | 0.00030298 | 2.0883e-05 | 3.8565e-06 | NA | NA | 0.00032772
Dichlorobenzene | 0.00043283 | 0.00029833 | 5.5093e-05 | NA | NA | 0.00078626
Ethylbenzene | 0.076743 | NA | NA | NA | NA | 0.076743
Fluoranthene | 1.0821e-06 | 7.4584e-07 | 1.3773e-07 | NA | NA | 1.9656e-06
Fluorene | 1.0099e-06 | 6.9611e-07 | 1.2855e-07 | NA | NA | 1.8346e-06
Formaldehyde | 7.2217 | 0.018646 | 0.0034433 | 7.6217e-05 | 0.0001239 | 7.244
Hexane | 0.64924 | 0.4475 | 0.08264 | NA | NA | 1.1794
Manganese | 0.0013706 | 9.4472e-05 | 1.7446e-05 | NA | NA | 0.0014825
Mercury | 0.0009378 | 6.4639e-05 | 1.1937e-05 | NA | NA | 0.0010144
Naphthalene | 0.0033377 | 0.00015165 | 2.8006e-05 | 0.00012558 | 8.904e-06 | 0.0036519
Nickel | 0.0075745 | 0.00052208 | 9.6413e-05 | NA | NA | 0.008193
Phenanathrene | 6.1317e-06 | 4.2264e-06 | 7.8049e-07 | NA | NA | 1.1139e-05
POM | 0.0052761 | NA | NA | 0.00020479 | 1.764e-05 | 0.0054985
Pyrene | 1.8035e-06 | 1.2431e-06 | 2.2956e-07 | NA | NA | 3.2761e-06
Toluene | 0.313 | 0.00084528 | 0.0001561 | 0.00027145 | 4.2945e-05 | 0.31431
Xylenes | 0.15349 | NA | NA | 0.00018644 | 2.9925e-05 | 0.1537
Maximum Emissions (Single HAP) | [5 empty] | 7.244
Total HAPs | [5 empty] | 9.1418
NA = No Emission Factor Available.
Global Warming Potential - CO2 | 1
Global Warming Potential - CH4 | 25
Global Warming Potential - N2O | 298
Global Warming Potential - SF6 | 22800

## CCCT_RevI_Steady State
ESC Brooke County Power I, LLC |  |  | Pollutant | Maximum Hourly (Short-Term) Emissions(1) | Maximum Annual SS Emissions | Startup and Shutdown Emissions(2), (3) | Maximum Annual SS Emissions, Excluding SUSD Duration | Maximum Annual SS Emissions, Including SUSD Emissions | Maximum Annual Steady State Emissions(4), (5) | Maximum Hourly (Short-Term) Emissions | Maximum Annual Steady State Emissions | Emission Concentration for WVDEP Form J |  | Pre-Control Emissions for WVDEP Form J
Emission Calculations - Combined Cycle Units
|  |  |  | 1 CT/DB | 1 CT/DB | 1 CT/DB | 1 CT/DB | 1 CT/DB | 1 CT/DB | 2 CTs/DBs
Input Data |  |  |  |  | 8760 hr/yr | 159 hr/yr | 8601 hr/yr | 8,601+159 hr/yr |  |  |  | 1 CT/DB |  | Removal Efficiency | 1 CT/DB |  | 2 CTs/DBs
No. of Combustion Turbines | 2 |  |  | lb/hr | (tons/yr) | (tons/yr) | (tons/yr) | (tons/yr) | (tons/yr) | lb/hr | ton/yr | mg/min | mg/m3 | % | lb/hr | ton/yr | lb/hr | ton/yr
Natural Gas Heating Value (Btu/lb - HHV) | 23340 |  | VOC | 8.1 | 35.478 | 7.674 | 34.834 | 42.508 | 34.834 | 16.2 | 69.6681 | 61222.5 | 1.6324 | 30% | 11.5714 | 50.6829 | 23.1429 | 99.5259
Natural Gas Heating Value (Btu/lb - LHV) | 21089 |  | NOx | 23.2 | 101.616 | 13.67 | 99.7716 | 113.4416 | 99.7716 | 46.4 | 199.5432 | 175353.3333 | 4.6755 | 90% | 232 | 1016.16 | 464 | 1995.432
LHV-HHV Conversion Factor (Natural Gas) | 1.1067 |  | CO | 14.1 | 61.758 | 61.19 | 60.6371 | 121.8271 | 60.6371 | 28.2 | 121.2741 | 106572.5 | 2.8416 | 80% | 70.5 | 308.79 | 141 | 606.3705
Natural Gas Heating Value (Btu/scf) | 1030 |  | SO2 | 4 | 17.52 |  | 17.202 | 17.202 | 17.52 | 8 | 35.04 | 30233.3333 | 0.80612 | 0% | 4 | 17.52 | 8 | 35.04
Ethane Heating Value (Btu/lb - HHV) | 22728 |  | PM/PM10/PM2.5 | 16.9 | 74.022 | 1.8808 | 72.6785 | 74.5593 | 72.6785 | 33.8 | 145.3569 | 127735.8333 | 3.4059 | 0% | 16.9 | 74.022 | 33.8 | 145.3569
Ethane Heating Value (Btu/lb - LHV) | 20694 |  | Pb(6) | 0.001329 | 0.0058209 |  | 0.0057153 | 0.0057153 | 0.0058209 | 0.002658 | 0.011642 | 10.0449 | 0.00026783 | 0% | 0.001329 | 0.0058209 | 0.002658 | 0.011642
LHV-HHV Conversion Factor (Ethane) | 1.0983 |  | H2SO4(7) | 2.6 | 11.388 |  | 11.1813 | 11.1813 | 11.388 | 5.2 | 22.776 | 19651.6667 | 0.52398 | 0% | 2.6 | 11.388 | 5.2 | 22.776
Ethane Heating Value (Btu/scf) | 1783 |  | CO2(7) | 417000 | 1826460 |  | 1793308.5 | 1793308.5 | 1826460 | 834000 | 3652920 | 3151825000 | 84038.0904 | 0% | 417000 | 1826460 | 834000 | 3652920
CT Annual Capacity Factor (%) | 100% |  | CH4(8) | 6.9686 | 30.5224 |  | 29.9684 | 29.9684 | 30.5224 | 13.9372 | 61.0448 | 52670.8759 | 1.4044 | 0% | 6.9686 | 30.5224 | 13.9372 | 61.0448
CT Annual Operating Hours (hr/yr) | 8760 |  | N2O(8) | 0.69686 | 3.0522 |  | 2.9968 | 2.9968 | 3.0522 | 1.3937 | 6.1045 | 5267.0876 | 0.14044 | 0% | 0.69686 | 3.0522 | 1.3937 | 6.1045
Max. Heat Input, CT (MMBtu/hr) (HHV, all conditions) | 2737.7 |  | GHG (Mass Basis)(9) | 417007.6654 | 1826493.5746 |  | 1793341.4652 | 1793341.4652 | 1826493.5746 | 834015.3309 | 3652987.1493 | 3151882937.9635 | 84039.6352 | 0% | 417007.6654 | 1826493.5746 | 834015.3309 | 3652987.1493
Max. Heat Input, DB (MMBtu/hr) (HHV, all conditions) | 424.1 |  | GHG (CO2e Basis)(10), (11) | 417381.8784 | 1828132.6273 |  | 1794950.7679 | 1794950.7679 | 1828132.6273 | 834763.7567 | 3656265.2545 | 3154711363.9983 | 84115.0504 | 0% | 417381.8784 | 1828132.6273 | 834763.7567 | 3656265.2545
Max. Heat Input CT + DB (MMBtu/hr) (HHV, all conditions) | 3161.8
Max. Heat Input CT + DB (MMBtu/yr) (HHV, all conditions) | 27697368 |  | (1) Potential short-term (lb/hr) emission rates are based on the GE data (RevI T218), which encompasses the expected range of combustion turbine operating loads and conditions (i.e., fuel type, temperature, evaporative cooling, duct firing, etc.). Potential short-term emission rates for NOx, CO, SO2, PM, PM10, PM2.5, VOC, H2SO4, and CO2 for the CTs/DBs are established by selecting the maximum lb/hr emission rates across all fuel types, operating loads, and ambient temperature ranges. SO2 & H2SO4 emissions reflect a fuel sulfur content specification of 0.4 grains per 100 standard cubic feet (gr/100 scf) when firing any fuel.
CT Annual SUSD Hours (hr/yr), all events, per CT | 159
Pb Emission Factor (lb/MMscf) | 0.0005 |  | (2) In order to eliminate minor double-counting of emissions from both startups and shutdowns and steady-state emissions, the potential annual emissions proposed for NOx, CO, VOC, and PM/PM10/PM2.5, are based on excluding the duration (159 hr/yr) of off-line hours that would be associated with those start-ups and shutdowns.
Global Warming Potential - CO2 | 1 |  | (3) Startup and shutdown emission rates are not available for SO2, Pb, H2SO4, or GHGs. Worst-case emissions for those pollutants are assumed to be steady-state operation for 8,760 hr/yr.
Global Warming Potential - CH4 | 25 |  | (4) For NOx, CO, VOC, and PM/PM10/PM2.5, maximum steady-state emissions are based on 8,601 hr/yr, which excludes 159 hours allotted for SUSD events, where Tons/yr = (Maximum lb/hr) x (8,601 hr/yr) x (1 ton/2000 lb).
Global Warming Potential - N2O | 298 |  | (5) For all other pollutants, Tons/yr = (Maximum lb/hr) x (8,760 hr/yr) x (1 ton/2000 lb).
40 CFR Part 98 Subpart C Emission Factors for GHG Pollutants(4) |  |  | (6) Pb emission factor from USEPA's AP-42, Section 1.4.
| Natural Gas | Ethane | (7) Based on the emissions and performance data provided by GE.
Conversion Factor (kg to lb) | 2.2046 | 2.2046 | (8) Default emission factors obtained from 40 CFR Part 98, Subpart C: General Stationary Fuel Combustion Sources, Tables C-1 and C-2 for natural gas firing.
CO2 Emission Factor (kg/MMBtu) | 53.06 | 59.6 | (9) The sum of potential annual GHG emissions on a mass basis (i.e., no GWP applied).
CO2 Emission Factor (lb/MMBtu) | 116.9771 | 131.3954 | (10) For each GHG, emissions are normalized to a CO2e basis by multiplying the mass emissions of each individual GHG pollutant by its respective Global warming potentials (GWP). GWP of each pollutant established by 40 CFR Part 98, Subpart A: General Provisions, Table A-1.
CH4 Emission Factor (kg/MMBtu) | 0.001 | 0.003
CH4 Emission Factor (lb/MMBtu) | 0.0022046 | 0.0066139
N2O Emission Factor (kg/MMBtu) | 0.0001 | 0.0006 | (11) The sum of potential annual GHG emissions on a CO2e basis.
N2O Emission Factor (lb/MMBtu) | 0.00022046 | 0.0013228
Maximum Hourly Fuel Use (SCF/hr) | 2657961.165 | 1535445.8777
Maximum Annual Fuel Use (MMSCF/yr) | 23283.7398 | 13450.5059

## RevI_Project HAPS
ESC Brooke County Power I, LLC
Emission Calculations - HAPs
Parameters | Units | CT(1) | DB | Auxiliary Boiler | Fuel Gas Heater | Emergency Generator | Fire Water Pump | CT Organic HAP Control Efficiency(2) |  | Emission Concentrations for Attachment J
Maximum Heat Input | MMBtu/hr | 2737.7 | 424.1 | 111.9188 | 5.3982 | 19.32 | 2.1 | 90%
Maximum Annual Operation | hr/yr | 8760 | 8760 | 4576 | 8760 | 100 | 100 |  |  | Conversions | g/lb | 453.592
(1) Expected heat input at an ambient temperature of 10 °F. | [10 empty] | m/ft | 0.3048
HAP | CT Emission Factor(1) (lb/MMBtu) | DB Emission Factor (2) (lb/MMscf) | One CT (lb/hr) | One DB (lb/hr) | One CT + One DB (lb/hr) | Two CT (lb/hr) | Two DB (lb/hr) | Two CT + Two DB (lb/hr) | One CT (tons/yr) | One DB (tons/yr) | One CT + One DB (tons/yr) | Two CTs (tons/yr) | Two DB (tons/yr) | Two CT + Two DB (tons/yr) | CT Emissions (mg/min) | CT Emissions (mg/m3) | DB Emissions (mg/min) | DB Emissions (mg/m3) | CT + DB Emissions (mg/m3) | Uncontrolled One CT (lb/hr) | Uncontrolled One DB (lb/hr) | Uncontrolled One CT + One DB (lb/hr) | Uncontrolled One CT + One DB (ton/yr)
2-Methylnaphthalene | NA | 2.4e-05 | NA | 9.8819e-07 | 9.8819e-07 | NA | 1.9764e-06 | 1.9764e-06 | NA | 4.3283e-06 | 4.3283e-06 | NA | 8.6566e-06 | 8.6566e-06 | NA | NA | 0.0074706 | 1.9919e-07 | 1.9919e-07 | NA | 9.8819e-06 | 9.8819e-06 | 4.3283e-05
Acetaldehyde | 4e-05 | NA | 0.010951 | NA | 0.010951 | 0.021902 | NA | 0.021902 | 0.047965 | NA | 0.047965 | 0.095929 | NA | 0.095929 | 82.7866 | 0.0022074 | NA | NA | 0.0022074 | 0.10951 | NA | 0.10951 | 0.47965
Acrolein | 6.4e-06 | NA | 0.0017521 | NA | 0.0017521 | 0.0035043 | NA | 0.0035043 | 0.0076743 | NA | 0.0076743 | 0.015349 | NA | 0.015349 | 13.2459 | 0.00035318 | NA | NA | 0.00035318 | 0.017521 | NA | 0.017521 | 0.076743
Arsenic | NA | 0.0002 | NA | 8.235e-05 | 8.235e-05 | NA | 0.0001647 | 0.0001647 | NA | 0.00036069 | 0.00036069 | NA | 0.00072138 | 0.00072138 | NA | NA | 0.62255 | 1.6599e-05 | 1.6599e-05 | NA | 8.235e-05 | 8.235e-05 | 0.00036069
Benzene | 1.2e-05 | 0.0021 | 0.0032852 | 8.6467e-05 | 0.0033717 | 0.0065705 | 0.00017293 | 0.0067434 | 0.014389 | 0.00037873 | 0.014768 | 0.028779 | 0.00075745 | 0.029536 | 24.836 | 0.00066221 | 0.65368 | 1.7429e-05 | 0.00067964 | 0.032852 | 0.00086467 | 0.033717 | 0.14768
Cadmium | NA | 0.0011 | NA | 0.00045292 | 0.00045292 | NA | 0.00090584 | 0.00090584 | NA | 0.0019838 | 0.0019838 | NA | 0.0039676 | 0.0039676 | NA | NA | 3.424 | 9.1296e-05 | 9.1296e-05 | NA | 0.00045292 | 0.00045292 | 0.0019838
Chromium | NA | 0.0014 | NA | 0.00057645 | 0.00057645 | NA | 0.0011529 | 0.0011529 | NA | 0.0025248 | 0.0025248 | NA | 0.0050497 | 0.0050497 | NA | NA | 4.3579 | 0.00011619 | 0.00011619 | NA | 0.00057645 | 0.00057645 | 0.0025248
Cobalt | NA | 8.4e-05 | NA | 3.4587e-05 | 3.4587e-05 | NA | 6.9174e-05 | 6.9174e-05 | NA | 0.00015149 | 0.00015149 | NA | 0.00030298 | 0.00030298 | NA | NA | 0.26147 | 6.9717e-06 | 6.9717e-06 | NA | 3.4587e-05 | 3.4587e-05 | 0.00015149
Dichlorobenzene | NA | 0.0012 | NA | 4.941e-05 | 4.941e-05 | NA | 9.8819e-05 | 9.8819e-05 | NA | 0.00021641 | 0.00021641 | NA | 0.00043283 | 0.00043283 | NA | NA | 0.37353 | 9.9596e-06 | 9.9596e-06 | NA | 0.0004941 | 0.0004941 | 0.0021641
Ethylbenzene | 3.2e-05 | NA | 0.0087606 | NA | 0.0087606 | 0.017521 | NA | 0.017521 | 0.038372 | NA | 0.038372 | 0.076743 | NA | 0.076743 | 66.2293 | 0.0017659 | NA | NA | 0.0017659 | 0.087606 | NA | 0.087606 | 0.38372
Fluoranthene | NA | 3e-06 | NA | 1.2352e-07 | 1.2352e-07 | NA | 2.4705e-07 | 2.4705e-07 | NA | 5.4104e-07 | 5.4104e-07 | NA | 1.0821e-06 | 1.0821e-06 | NA | NA | 0.00093383 | 2.4899e-08 | 2.4899e-08 | NA | 1.2352e-06 | 1.2352e-06 | 5.4104e-06
Fluorene | NA | 2.8e-06 | NA | 1.1529e-07 | 1.1529e-07 | NA | 2.3058e-07 | 2.3058e-07 | NA | 5.0497e-07 | 5.0497e-07 | NA | 1.0099e-06 | 1.0099e-06 | NA | NA | 0.00087157 | 2.3239e-08 | 2.3239e-08 | NA | 1.1529e-06 | 1.1529e-06 | 5.0497e-06
Formaldehyde | 0.0003 | 0.075 | 0.82131 | 0.0030881 | 0.8244 | 1.6426 | 0.0061762 | 1.6488 | 3.5973 | 0.013526 | 3.6109 | 7.1947 | 0.027052 | 7.2217 | 6208.9941 | 0.16555 | 23.3457 | 0.00062247 | 0.16617 | 8.2131 | 0.030881 | 8.244 | 36.1086
Hexane | NA | 1.8 | NA | 0.074115 | 0.074115 | NA | 0.14823 | 0.14823 | NA | 0.32462 | 0.32462 | NA | 0.64924 | 0.64924 | NA | NA | 560.2962 | 0.014939 | 0.014939 | NA | 0.74115 | 0.74115 | 3.2462
Manganese | NA | 0.00038 | NA | 0.00015646 | 0.00015646 | NA | 0.00031293 | 0.00031293 | NA | 0.00068531 | 0.00068531 | NA | 0.0013706 | 0.0013706 | NA | NA | 1.1828 | 3.1539e-05 | 3.1539e-05 | NA | 0.00015646 | 0.00015646 | 0.00068531
Mercury | NA | 0.00026 | NA | 0.00010705 | 0.00010705 | NA | 0.00021411 | 0.00021411 | NA | 0.0004689 | 0.0004689 | NA | 0.0009378 | 0.0009378 | NA | NA | 0.80932 | 2.1579e-05 | 2.1579e-05 | NA | 0.00010705 | 0.00010705 | 0.0004689
Naphthalene | 1.3e-06 | 0.00061 | 0.0003559 | 2.5117e-05 | 0.00038102 | 0.0007118 | 5.0233e-05 | 0.00076204 | 0.0015588 | 0.00011001 | 0.0016689 | 0.0031177 | 0.00022002 | 0.0033377 | 2.6906 | 7.1739e-05 | 0.18988 | 5.0628e-06 | 7.6802e-05 | 0.003559 | 0.00025117 | 0.0038102 | 0.016689
Nickel | NA | 0.0021 | NA | 0.00086467 | 0.00086467 | NA | 0.0017293 | 0.0017293 | NA | 0.0037873 | 0.0037873 | NA | 0.0075745 | 0.0075745 | NA | NA | 6.5368 | 0.00017429 | 0.00017429 | NA | 0.00086467 | 0.00086467 | 0.0037873
Phenanathrene | NA | 1.7e-05 | NA | 6.9997e-07 | 6.9997e-07 | NA | 1.3999e-06 | 1.3999e-06 | NA | 3.0659e-06 | 3.0659e-06 | NA | 6.1317e-06 | 6.1317e-06 | NA | NA | 0.0052917 | 1.4109e-07 | 1.4109e-07 | NA | 6.9997e-06 | 6.9997e-06 | 3.0659e-05
POM | 2.2e-06 | NA | 0.00060229 | NA | 0.00060229 | 0.0012046 | NA | 0.0012046 | 0.002638 | NA | 0.002638 | 0.0052761 | NA | 0.0052761 | 4.5533 | 0.00012141 | NA | NA | 0.00012141 | 0.0060229 | NA | 0.0060229 | 0.02638
Pyrene | NA | 5e-06 | NA | 2.0587e-07 | 2.0587e-07 | NA | 4.1175e-07 | 4.1175e-07 | NA | 9.0173e-07 | 9.0173e-07 | NA | 1.8035e-06 | 1.8035e-06 | NA | NA | 0.0015564 | 4.1498e-08 | 4.1498e-08 | NA | 2.0587e-06 | 2.0587e-06 | 9.0173e-06
Toluene | 0.00013 | 0.0034 | 0.03559 | 0.00013999 | 0.03573 | 0.07118 | 0.00027999 | 0.07146 | 0.15588 | 0.00061317 | 0.1565 | 0.31177 | 0.0012263 | 0.313 | 269.0564 | 0.0071739 | 1.0583 | 2.8219e-05 | 0.0072022 | 0.3559 | 0.0013999 | 0.3573 | 1.565
Xylenes | 6.4e-05 | NA | 0.017521 | NA | 0.017521 | 0.035043 | NA | 0.035043 | 0.076743 | NA | 0.076743 | 0.15349 | NA | 0.15349 | 132.4585 | 0.0035318 | NA | NA | 0.0035318 | 0.17521 | NA | 0.17521 | 0.76743
NA = No Emission Factor Available. | [20 empty] | 42.8303
(1) Combustion Turbine (CT) HAP Emission Factors obtained from EPA's AP-42 Section 3.1, except formaldehyde, which is based on the EPA 95th upper percentile emission factor for CTGs (EPA August 21, 2001 memorandum). The formaldehyde emission factor of 3.0E-04 was obtained by taking the formaldehyde factor in Table 3 of the 8/21/2001 memo of 2.92E-03 lb/MMBtu and applying a control efficiency of 90% to account for the use of Oxidation Catalysts. This value was rounded to 3.0E-04.
(2) Duct Burner (DB) HAP emission factors obtained from EPA's AP-42 Chapter 1.4, Tables 1.4-3 and 1.4-4.
(3) A control efficiency of 90% was applied to CT & DB organic HAP emissions to account for the use of Oxidation Catalysts, with the exception of the CT formaldehyde emissions, which are calculated using a controlled factor.
Hazardous Air Pollutant (HAP) | One CT (lb/hr) | One DB (lb/hr) | Auxiliary Boiler (lb/hr) | Fuel Gas Heater (lb/hr) | Emergency Generator (lb/hr) | Fire Water Pump (lb/hr) | Two CT + Two DB (tons/yr) | Auxiliary Boiler (tons/yr) | Fuel Gas Heaters (2) (tons/yr) | Emergency Generator (tons/yr) | Fire Water Pump (tons/yr) | Facility Total (tons/yr)
2-Methylnaphthalene | NA | 9.8819e-07 | 2.6078e-06 | 1.2578e-07 | NA | NA | 8.6566e-06 | 5.9667e-06 | 1.1019e-06 | NA | NA | 1.5725e-05
Acetaldehyde | 0.010951 | NA | NA | NA | 0.00048686 | 0.0016107 | 0.095929 | NA | NA | 2.4343e-05 | 8.0535e-05 | 0.096034
Acrolein | 0.0017521 | NA | NA | NA | 0.00015224 | 0.000788 | 0.015349 | NA | NA | 7.6121e-06 | 1.182e-06 | 0.015357
Arsenic | NA | 8.235e-05 | 2.1732e-05 | 1.0482e-06 | NA | NA | 0.00072138 | 4.9722e-05 | 9.1822e-06 | NA | NA | 0.00078029
Benzene | 0.0032852 | 8.6467e-05 | 0.00022818 | 1.1006e-05 | 0.014992 | 0.0019593 | 0.029536 | 0.00052208 | 9.6413e-05 | 0.00074962 | 9.7965e-05 | 0.031002
Cadmium | NA | 0.00045292 | NA | NA | NA | NA | 0.0039676 | NA | NA | NA | NA | 0.0039676
Chromium | NA | 0.00057645 | 0.00015212 | 7.3374e-06 | NA | NA | 0.0050497 | 0.00034806 | 6.4276e-05 | NA | NA | 0.005462
Cobalt | NA | 3.4587e-05 | 9.1274e-06 | 4.4024e-07 | NA | NA | 0.00030298 | 2.0883e-05 | 3.8565e-06 | NA | NA | 0.00032772
Dichlorobenzene | NA | 4.941e-05 | 0.00013039 | 6.2892e-06 | NA | NA | 0.00043283 | 0.00029833 | 5.5093e-05 | NA | NA | 0.00078626
Ethylbenzene | 0.0087606 | NA | NA | NA | NA | NA | 0.076743 | NA | NA | NA | NA | 0.076743
Fluoranthene | NA | 1.2352e-07 | 3.2598e-07 | 1.5723e-08 | NA | NA | 1.0821e-06 | 7.4584e-07 | 1.3773e-07 | NA | NA | 1.9656e-06
Fluorene | NA | 1.1529e-07 | 3.0425e-07 | 1.4675e-08 | NA | NA | 1.0099e-06 | 6.9611e-07 | 1.2855e-07 | NA | NA | 1.8346e-06
Formaldehyde | 0.82131 | 0.0030881 | 0.0081494 | 0.00039307 | 0.0015243 | 0.002478 | 7.2217 | 0.018646 | 0.0034433 | 7.6217e-05 | 0.0001239 | 7.244
Hexane | NA | 0.074115 | 0.19559 | 0.0094338 | NA | NA | 0.64924 | 0.4475 | 0.08264 | NA | NA | 1.1794
Manganese | NA | 0.00015646 | 4.129e-05 | 1.9916e-06 | NA | NA | 0.0013706 | 9.4472e-05 | 1.7446e-05 | NA | NA | 0.0014825
Mercury | NA | 0.00010705 | 2.8251e-05 | 1.3627e-06 | NA | NA | 0.0009378 | 6.4639e-05 | 1.1937e-05 | NA | NA | 0.0010144
Naphthalene | 0.0003559 | 2.5117e-05 | 6.6282e-05 | 3.197e-06 | 0.0025116 | 0.00017808 | 0.0033377 | 0.00015165 | 2.8006e-05 | 0.00012558 | 8.904e-06 | 0.0036519
Nickel | NA | 0.00086467 | 0.00022818 | 1.1006e-05 | NA | NA | 0.0075745 | 0.00052208 | 9.6413e-05 | NA | NA | 0.008193
Phenanathrene | NA | 6.9997e-07 | 1.8472e-06 | 8.9097e-08 | NA | NA | 6.1317e-06 | 4.2264e-06 | 7.8049e-07 | NA | NA | 1.1139e-05
POM | 0.00060229 | NA | NA | NA | 0.0040958 | 0.0003528 | 0.0052761 | NA | NA | 0.00020479 | 1.764e-05 | 0.0054985
Pyrene | NA | 2.0587e-07 | 5.433e-07 | 2.6205e-08 | NA | NA | 1.8035e-06 | 1.2431e-06 | 2.2956e-07 | NA | NA | 3.2761e-06
Toluene | 0.03559 | 0.00013999 | 0.00036944 | 1.7819e-05 | 0.0054289 | 0.0008589 | 0.313 | 0.00084528 | 0.0001561 | 0.00027145 | 4.2945e-05 | 0.31431
Xylenes | 0.017521 | NA | NA | NA | 0.0037288 | 0.0005985 | 0.15349 | NA | NA | 0.00018644 | 2.9925e-05 | 0.1537
Maximum Emissions (Single HAP) | [11 empty] | 7.244
Total HAPs | 0.90013 | 0.07978 | 0.20502 | 0.0098886 | 0.032921 | 0.0088243 | 8.584 | 0.46908 | 0.086625 | 0.001646 | 0.000403 | 9.1418
NA = No Emission Factor Available.

## CT Startups&Shutdowns
ESC Brooke County Power I, LLC
Emission Calculations - Combustion Turbine Startups and Shutdowns - Rapid Response Lite(1)
Type(2) | Pollutant | Emissions (lb/event) | Duration (min/event) | No. of Events per Year | Total Duration (hr/yr) | Emissions (lb/yr) | Emissions from 1 CT (tons/yr) | Emissions from 2 CTs (tons/yr)
NOx
RRL Startups | Hot | 70 | 20 | 208 | 69.3333 | 14560 | 7.28 | 14.56
| Warm | 175 | 40 | 40 | 26.6667 | 7000 | 3.5 | 7
| Cold | 330 | 55 | 12 | 11 | 3960 | 1.98 | 3.96
Conventional | (Lead Conventional, Lag Cold) | 1300 | 240 | 0 | 0 | 0 | 0 | 1.98
Shutdowns |  | 7 | 12 | 260 | 52 | 1820 | 0.91 | 1.82
| Total |  |  |  | 159 | 27340 | 13.67 | 27.34
CO
RRL Startups | Hot | 310 | 20 | 208 | 69.3333 | 64480 | 32.24 | 64.48
| Warm | 350 | 40 | 40 | 26.6667 | 14000 | 7 | 14
| Cold | 950 | 55 | 12 | 11 | 11400 | 5.7 | 11.4
Conventional | (Lead Conventional, Lag Cold) | 8500 | 240 | 2 | 8 | 17000 | 8.5 | 14.2
Shutdowns |  | 125 | 12 | 260 | 52 | 32500 | 16.25 | 32.5
| Total |  |  |  | 159 | 122380 | 61.19 | 122.38
VOC (as Methane)
RRL Startups | Hot | 28 | 20 | 208 | 69.3333 | 5824 | 2.912 | 5.824
| Warm | 30 | 40 | 40 | 26.6667 | 1200 | 0.6 | 1.2
| Cold | 87 | 55 | 12 | 11 | 1044 | 0.522 | 1.044
Conventional | (Lead Conventional, Lag Cold) | 910 | 240 | 0 | 0 | 0 | 0 | 0.522
Shutdowns |  | 28 | 12 | 260 | 52 | 7280 | 3.64 | 7.28
| Total |  |  |  | 159 | 15348 | 7.674 | 15.348
PM/PM10/PM2.5
RRL Startups | Hot | 3.9 | 20 | 208 | 69.3333 | 811.2 | 0.4056 | 0.8112
| Warm | 7.9 | 40 | 40 | 26.6667 | 316 | 0.158 | 0.316
| Cold | 10.8 | 55 | 12 | 11 | 129.6 | 0.0648 | 0.1296
Conventional | (Lead Conventional, Lag Cold) | 48 | 240 | 0 | 0 | 0 | 0 | 0.0648
Shutdowns |  | 2.4 | 12 | 260 | 52 | 624 | 0.312 | 0.624
| Total |  |  |  | 159 | 1880.8 | 0.9404 | 1.8808
(1) The plant is started using GE’s Rapid Response Lite auto-start sequence. Prior to start, the plant is in a ready-to-start condition, i.e. all plant equipment which is needed to be operating during startup is in a no-fault condition, operational and/or in automatic mode. Water levels and pressures in drums, hotwell and other vessels are within range and/or not in an alarmed condition. Steam turbine sealing steam is on and condenser vacuum is within the range required for steam turbine startup. GT and HRSG Purge credit are available.
(2) Startup and shutdown emission rates obtained from GE performance data.
(3) Startup and shutdown emission rates were not calculated for SO2, Pb, H2SO4, or GHGs. Worst-case emissions for those pollutants were assumed to be steady-state operation.

## Auxiliary Boiler
ESC Brooke County Power I, LLC
Emission Calculations - Auxiliary Boiler
Parameter | Value (Natural Gas) | Value (Ethane)
Natural Gas Heating Value (Btu/scf) | 1030 | 1783
Maximum Heat Input (MMBtu/hr): | 111.9188 | 111.9188
Maximum Heat Input (Btu/hr) | 111918770 | 111918770
Maximum Hourly Fuel Use (scf/hr) | 108659 | 62769.9215
Maximum Hourly Fuel Use (MMscf/hr) | 0.10866 | 0.06277
Maximum Annual Fuel Use (MMscf/yr) | 497.2236 | 287.2352
Maximum Annual Fuel Use (MMBtu/yr) | 512140.2915 | 512140.2915
Maximum Annual Operation (hr/yr) | 4576 | 4576
Fuel Sulfur Content (gr/scf) | 0.4
Fuel Sulfur Content, by mass (ppm) | 12.4
Conversion Factor (gr/lb) | 7000
Conversion Factor SO2 to SO3 | 5%
Conversion Factor SO3 to H2SO4 | 100%
Molecular weight of S | 32
Molecular weight of SO2 | 64
Molecular weight of SO3 | 80
Molecular weight of H2SO4 | 98
Global Warming Potential - CO2 | 1
Global Warming Potential - CH4 | 25
Global Warming Potential - N2O | 298
40 CFR Part 98 Subpart C Emission Factors for GHG Pollutants(5)
| Natural Gas | Ethane
Conversion Factor (kg to lb) | 2.2046 | 2.2046
CO2 Emission Factor (kg/MMBtu) | 53.06 | 59.6
CO2 Emission Factor (lb/MMBtu) | 116.9771 | 131.3954
CH4 Emission Factor (kg/MMBtu) | 0.001 | 0.003
CH4 Emission Factor (lb/MMBtu) | 0.0022046 | 0.0066139
N2O Emission Factor (kg/MMBtu) | 0.0001 | 0.0006
N2O Emission Factor (lb/MMBtu) | 0.00022046 | 0.0013228 |  |  |  | Pre-Control Emissions
[6 empty] | Removal Efficiency | Aux Boiler
Pollutant | Emission Factor (lb/MMBtu)(2, 5) | Emissions (lb/hr) | Emissions (tons/yr) | Emissions (mg/min) | Emissions (mg/m3) | % | lb/hr | ton/yr
VOC | 0.008 | 0.89535 | 2.0486 | 6768.7278 | 11.9968 | 0% | 0.89535 | 2.0486
NOx | 0.011 | 1.2311 | 2.8168 | 9307.0008 | 16.4955 | 0% | 1.2311 | 2.8168
CO | 0.037 | 4.141 | 9.4746 | 31305.3662 | 55.485 | 0% | 4.141 | 9.4746
SO2 (3) | 0.0012958 | 0.14502 | 0.3318 | 1096.3278 | 1.9431 | 0% | 0.14502 | 0.3318
PM (1)/PM10/PM2.5 | 0.0077741 | 0.87007 | 1.9907 | 6577.6304 | 11.6581 | 0% | 0.87007 | 1.9907
Pb | 4.8544e-07 | 5.433e-05 | 0.00012431 | 0.41072 | 0.00072796 | 0% | 5.433e-05 | 0.00012431
H2SO4(4) | 9.9206e-05 | 0.011103 | 0.025404 | 83.9376 | 0.14877 | 0% | 0.011103 | 0.025404
CO2 (5) | 131.3954 | 14705.6062 | 33646.4269 | 111172421.97 | 197039.7506 | 0% | 14705.6062 | 33646.4269
CH4 (5) | 0.0066139 | 0.74022 | 1.6936 | 5595.9273 | 9.9181 | 0% | 0.74022 | 1.6936
N2O (5) | 0.0013228 | 0.14804 | 0.33872 | 1119.1855 | 1.9836 | 0% | 0.14804 | 0.33872
GHG (Mass Basis) (6) | -- | 14706.4944 | 33648.4593 | 111179137.0827 | 197051.6523 | 0% | 14706.4944 | 33648.4593
GHG (CO2e Basis) (7, 8) | -- | 14768.2284 | 33789.7065 | 111645837.4179 | 197878.8225 | 0% | 14768.2284 | 33789.7065
(1) PM emission factor includes filterable and condensable fractions.
(2) Emission factors obtained from potential vendor.
(3) SO2 lb/hr emission rate calculated as a mass balance based on fuel consumption and a maximum fuel sulfur content of 0.4 gr/100 scf.
(4) Exhaust emissions are based on 95% fuel sulfur conversion to SO2 and 5% fuel sulfur conversion to SO3. Sulfuric acid mist (H2SO4) emission calculations conservatively assume that all SO3 combines with water to form sulfur mist. SO3 = SO2 emissions (lb/hr) * 5% * MW SO3/MW SO2 H2SO4 = SO3 emissions (lb/hr) * 100% * MW H2SO4/MW SO3
(5) Default emission factors obtained from 40 CFR Part 98, Subpart C: General Stationary Fuel Combustion Sources, Tables C-1 and C-2 for natural gas firing and ethane combustion. Per Table C-2, the default CH4 and N2O factors for ethane combustion are those for "Petroleum".
(6) The sum of potential annual GHG emissions on a mass basis (i.e., no GWP applied).
(7) For each GHG, emissions are normalized to a CO2e basis by multiplying the mass emissions of each individual GHG pollutant by its respective Global warming potentials (GWP). GWP of each pollutant established by 40 CFR Part 98, Subpart A: General Provisions, Table A-1.
(8) The sum of potential annual GHG emissions on a CO2e basis.
Hazardous Air Pollutants
Pollutant | Emission Factor (lb/MMscf) (1) | Emissions (lb/hr) | Emissions (tons/yr) | Emissions (mg/min)(2) | Emissions (mg/m3)(3)
2-Methylnaphthalene | 2.4e-05 | 2.6078e-06 | 5.9667e-06 | 0.019715 | 3.4942e-05
Arsenic | 0.0002 | 2.1732e-05 | 4.9722e-05 | 0.16429 | 0.00029118
Benzene | 0.0021 | 0.00022818 | 0.00052208 | 1.725 | 0.0030574
Cadmium | 0.0011 | 0.00011952 | 0.00027347 | 0.90359 | 0.0016015
Chromium | 0.0014 | 0.00015212 | 0.00034806 | 1.15 | 0.0020383
Cobalt | 8.4e-05 | 9.1274e-06 | 2.0883e-05 | 0.069002 | 0.0001223
Dichlorobenzene | 0.0012 | 0.00013039 | 0.00029833 | 0.98574 | 0.0017471
Fluoranthene | 3e-06 | 3.2598e-07 | 7.4584e-07 | 0.0024643 | 4.3678e-06
Fluorene | 2.8e-06 | 3.0425e-07 | 6.9611e-07 | 0.0023001 | 4.0766e-06
Formaldehyde | 0.075 | 0.0081494 | 0.018646 | 61.6086 | 0.10919
Hexane | 1.8 | 0.19559 | 0.4475 | 1478.6056 | 2.6207
Manganese | 0.00038 | 4.129e-05 | 9.4472e-05 | 0.31215 | 0.00055325
Mercury | 0.00026 | 2.8251e-05 | 6.4639e-05 | 0.21358 | 0.00037854
Naphthalene | 0.00061 | 6.6282e-05 | 0.00015165 | 0.50108 | 0.00088811
Nickel | 0.0021 | 0.00022818 | 0.00052208 | 1.725 | 0.0030574
Phenanathrene | 1.7e-05 | 1.8472e-06 | 4.2264e-06 | 0.013965 | 2.4751e-05
Pyrene | 5e-06 | 5.433e-07 | 1.2431e-06 | 0.0041072 | 7.2796e-06
Toluene | 0.0034 | 0.00036944 | 0.00084528 | 2.7929 | 0.0049501
(1) Emission factors obtained from AP-42, Ch. 1.4, Tables 1.4-3 and 1.4-4. Emission factors were not included for pollutants at or below the method detection limits, designated as "less than (<)" in AP-42 emission factor tables.
(2) Grams per Pound Conversion Factor | 453.592
(3) Based on stack exhaust flow rate of (ACFM) | 19925

## Fuel Gas Heaters
ESC Brooke County Power I, LLC
Emission Calculations - Fuel Gas Heaters
Parameter | Value (Natural Gas) | Value (Ethane)
Number of Fuel Gas Heaters | 2
Natural Gas Heating Value (Btu/scf) | 1030 | 1783
Maximum Heat Input (MMBtu/hr): | 5.3982 | 5.3982
Maximum Heat Input (Btu/hr) | 5398230 | 5398230
Maximum Annual Fuel Use (scf/hr) | 5241 | 3027.6108
Maximum Annual Fuel Use (MMscf/hr) | 0.005241 | 0.0030276
Maximum Annual Fuel Use (MMscf/yr) | 45.9112 | 26.5219
Maximum Annual Fuel Use (MMBtu/yr) | 47288.4948 | 47288.4948
Maximum Annual Operation (hr/yr) | 8760 | 8760
Natural Gas Fuel Sulfur Content (gr/scf) | 0.4
Natural Gas Fuel Sulfur Content, by mass (ppm) | 12.4
Conversion Factor (gr/lb) | 7000
Conversion Factor SO2 to SO3 | 5%
Conversion Factor SO3 to H2SO4 | 100%
Molecular weight of S | 32
Molecular weight of SO2 | 64
Molecular weight of SO3 | 80
Molecular weight of H2SO4 | 98
Global Warming Potential - CO2 | 1
Global Warming Potential - CH4 | 25
Global Warming Potential - N2O | 298
40 CFR Part 98 Subpart C Emission Factors for GHG Pollutants(5)
| Natural Gas | Ethane
Conversion Factor (kg to lb) | 2.2046 | 2.2046
CO2 Emission Factor (kg/MMBtu) | 53.06 | 59.6
CO2 Emission Factor (lb/MMBtu) | 116.9771 | 131.3954
CH4 Emission Factor (kg/MMBtu) | 0.001 | 0.003
CH4 Emission Factor (lb/MMBtu) | 0.0022046 | 0.0066139
N2O Emission Factor (kg/MMBtu) | 0.0001 | 0.0006
N2O Emission Factor (lb/MMBtu) | 0.00022046 | 0.0013228
Pollutant | Emission Factor (lb/MMBtu)(2, 5) | Emissions, per FGH (lb/hr) | Emissions, per FGH (tons/yr) | Emissions, 2 FGHs (lb/hr) | Emissions, 2 FGHs (tons/yr) | Emissions, per FGH (mg/min) | Emissions, per FGH (mg/m3)
VOC | 0.007 | 0.037788 | 0.16551 | 0.075575 | 0.33102 | 285.6693 | 10.4977
NOx | 0.036 | 0.19434 | 0.85119 | 0.38867 | 1.7024 | 1469.1564 | 53.9883
CO | 0.0388 | 0.20945 | 0.9174 | 0.4189 | 1.8348 | 1583.4241 | 58.1874
SO2 (3) | 0.0012958 | 0.0069948 | 0.030637 | 0.01399 | 0.061274 | 52.8797 | 1.9432
PM (1)/PM10/PM2.5 | 0.0077741 | 0.041967 | 0.18381 | 0.083933 | 0.36763 | 317.2619 | 11.6587
Pb | 4.8544e-07 | 2.6205e-06 | 1.1478e-05 | 5.241e-06 | 2.2956e-05 | 0.019811 | 0.000728
H2SO4(4) | 9.9206e-05 | 0.00053554 | 0.0023457 | 0.0010711 | 0.0046913 | 4.0486 | 0.14878
CO2 (5) | 131.3954 | 709.3023 | 3106.7442 | 1418.6047 | 6213.4884 | 5362231.0489 | 197050.3667
CH4 (5) | 0.0066139 | 0.035703 | 0.15638 | 0.071406 | 0.31276 | 269.911 | 9.9186
N2O (5) | 0.0013228 | 0.0071406 | 0.031276 | 0.014281 | 0.062552 | 53.9822 | 1.9837
GHG (Mass Basis) (6) | -- | 709.3452 | 3106.9319 | 1418.6903 | 6213.8637 | 5362554.9421 | 197062.269
GHG (CO2e Basis) (7, 8) | -- | 712.3228 | 3119.9739 | 1424.6456 | 6239.9479 | 5385065.516 | 197889.4838
(1) PM emission factor includes filterable and condensable fractions.
(2) Emission factors obtained from potential vendor.
(3) SO2 lb/hr emission rate calculated as a mass balance based on fuel consumption and a maximum fuel sulfur content of 0.4 gr/100 scf.
(4) Exhaust emissions are based on 95% fuel sulfur conversion to SO2 and 5% fuel sulfur conversion to SO3. Sulfuric acid mist (H2SO4) emission calculations conservatively assume that all SO3 combines with water to form sulfur mist. SO3 = SO2 emissions (lb/hr) * 5% * MW SO3/MW SO2 H2SO4 = SO3 emissions (lb/hr) * 100% * MW H2SO4/MW SO3
(5) Default emission factors obtained from 40 CFR Part 98, Subpart C: General Stationary Fuel Combustion Sources, Tables C-1 and C-2 for natural gas firing and ethane combustion. Per Table C-2, the default CH4 and N2O factors for ethane combustion are those for "Petroleum".
(6) The sum of potential annual GHG emissions on a mass basis (i.e., no GWP applied).
(7) For each GHG, emissions are normalized to a CO2e basis by multiplying the mass emissions of each individual GHG pollutant by its respective Global warming potentials (GWP). GWP of each pollutant established by 40 CFR Part 98, Subpart A: General Provisions, Table A-1.
(8) The sum of potential annual GHG emissions on a CO2e basis.
Hazardous Air Pollutants
Pollutant | Emission Factor (lb/MMscf) (1) | Emissions (lb/hr) | Emissions (tons/yr) | Emissions (mg/min)(2) | Emissions (mg/m3)(3)
2-Methylnaphthalene | 2.4e-05 | 1.2578e-07 | 5.5093e-07 | 0.00095091 | 3.4944e-05
Arsenic | 0.0002 | 1.0482e-06 | 4.5911e-06 | 0.0079243 | 0.0002912
Benzene | 0.0021 | 1.1006e-05 | 4.8207e-05 | 0.083205 | 0.0030576
Cadmium | 0.0011 | 5.7651e-06 | 2.5251e-05 | 0.043583 | 0.0016016
Chromium | 0.0014 | 7.3374e-06 | 3.2138e-05 | 0.05547 | 0.0020384
Cobalt | 8.4e-05 | 4.4024e-07 | 1.9283e-06 | 0.0033282 | 0.0001223
Dichlorobenzene | 0.0012 | 6.2892e-06 | 2.7547e-05 | 0.047546 | 0.0017472
Fluoranthene | 3e-06 | 1.5723e-08 | 6.8867e-08 | 0.00011886 | 4.368e-06
Fluorene | 2.8e-06 | 1.4675e-08 | 6.4276e-08 | 0.00011094 | 4.0768e-06
Formaldehyde | 0.075 | 0.00039307 | 0.0017217 | 2.9716 | 0.1092
Hexane | 1.8 | 0.0094338 | 0.04132 | 71.3183 | 2.6208
Manganese | 0.00038 | 1.9916e-06 | 8.7231e-06 | 0.015056 | 0.00055328
Mercury | 0.00026 | 1.3627e-06 | 5.9685e-06 | 0.010302 | 0.00037856
Naphthalene | 0.00061 | 3.197e-06 | 1.4003e-05 | 0.024169 | 0.00088816
Nickel | 0.0021 | 1.1006e-05 | 4.8207e-05 | 0.083205 | 0.0030576
Phenanathrene | 1.7e-05 | 8.9097e-08 | 3.9024e-07 | 0.00067356 | 2.4752e-05
Pyrene | 5e-06 | 2.6205e-08 | 1.1478e-07 | 0.00019811 | 7.28e-06
Toluene | 0.0034 | 1.7819e-05 | 7.8049e-05 | 0.13471 | 0.0049504
(1) Emission factors obtained from AP-42, Ch. 1.4, Tables 1.4-3 and 1.4-4. Emission factors were not included for pollutants at or below the method detection limits, designated as "less than (<)" in AP-42 emission factor tables.
(2) Grams per Pound Conversion Factor | 453.592
(3) Based on stack exhaust flow rate of (ACFM) | 961

## Emergency Generator
ESC Brooke County Power I, LLC
Emission Calculations - Emergency Generator (Tier 2)
Parameter | Value
Heating Value of ULSD (Btu/gal): | 140000
ULSD Sulfur Content (wt. %): | 0.0015
Rated Output (kW): | 2000
Rated Output (hp): | 2682
Fuel Consumption (gal/hr): | 138
Heat Input (MMBtu/hr): | 19.32
Maximum Annual Operation (hr/yr) | 100
NOx + NMHC Emission Factor (g/hp-hr) | 5.45
Concentration of NOx | 90%
Concentration of NMHC | 10%
Conversion Factor SO2 to SO3 | 10%
Conversion Factor SO3 to H2SO4 | 100%
Molecular weight of S | 32
Molecular weight of SO2 | 64
Molecular weight of SO3 | 80
Molecular weight of H2SO4 | 98
Fuel Oil Density (lb/gal) | 7.05
kg-lb Conversion Factor | 2.2046
CO2 Emission Factor (kg/MMBtu) | 73.96
CO2 Emission Factor (lb/MMBtu) | 163.0537
CH4 Emission Factor (kg/MMBtu) | 0.003
CH4 Emission Factor (lb/MMBtu) | 0.0066139
N2O Emission Factor (kg/MMBtu) | 0.0006
N2O Emission Factor (lb/MMBtu) | 0.0013228
Global Warming Potential - CO2 | 1
Global Warming Potential - CH4 | 25
Global Warming Potential - N2O | 298
Criteria Pollutants
Pollutant | Emission Factor (g/hp-hr) (1) | Emission Factor (lb/MMBtu) | Emissions (lb/hr) | Emissions (tons/yr) | Emissions (mg/min) | Emissions (mg/m3)
VOC | 0.11 | -- | 0.65041 | 0.032521 | 4917.0217 | 11.3529
NOx(2) | 5.45 | -- | 32.2249 | 1.6112 | 243616.0742 | 562.4858
CO | 0.3 | -- | 1.7738 | 0.088692 | 13410.0591 | 30.9625
SO2 | -- | 0.0015107 | 0.029187 | 0.0014594 | 220.6498 | 0.50946
PM/PM10/PM2.5 | 0.025 | -- | 0.14782 | 0.007391 | 1117.5049 | 2.5802
H2SO4(4) | -- | 0.00023133 | 0.0044693 | 0.00022346 | 33.787 | 0.078011
CO2(3) | -- | 163.0537 | 3150.1974 | 157.5099 | 23815072.2516 | 54986.6845
CH4(3) | -- | 0.0066139 | 0.12778 | 0.006389 | 965.9981 | 2.2304
N2O(3) | -- | 0.0013228 | 0.025556 | 0.0012778 | 193.1996 | 0.44608
GHG (Mass Basis)(6) | -- | -- | 3150.3507 | 157.5175 | 23816231.4493 | 54989.361
GHG (CO2e Basis)(4), (5), (7) | -- | -- | 3161.0076 | 158.0504 | 23896795.6878 | 55175.376
(1) Emission factors NOx, CO, PM, and VOC provided by vendor. SO2 lb/hr emission rate calculated as a mass balance and based on fuel consumption and fuel oil sulfur content.
(2) The NSPS Subpart IIII NOx + NMHC standard of 4.8 g/hp-hr is based on specific test procedures that engine manufacturers must use to certify their engines as NSPS compliant. These test procedures are outlined in 40 CFR 89 Subpart E (Exhaust Emission Test Procedures). These procedures involve testing an engine on a dynamometer in a test cycle, in a prescribed sequence of engine operating conditions that feature different time durations at different loads. These procedures require the determination of the concentration of each pollutant, exhaust volume, the fuel flow, and the power output during each operating mode. The measured values are weighted and used to calculate the g/hp-hr emission rate for each pollutant. Because the NSPS test is a weighted composite of emissions at various engine operating loads, it does not necessarily capture an engine’s worst-case emission rates. For air permitting purposes, the worst-case NOx emissions is 5.45 g/hp-hr, but the overall weighed emissions for the NSPS test–cycle are below the 4.8 g/hp-hr NOx + NMHC standard.
(3) Default emission factors obtained from 40 CFR Part 98, Subpart C: General Stationary Fuel Combustion Sources, Tables C-1 and C-2 for distillate fuel oil No. 2 firing.
(4) Global warming potentials (GWP) of each pollutant established by 40 CFR Part 98, Subpart A: General Provisions, Table A-1.
(5) For each GHG, emissions are normalized to a CO2e basis by multiplying the mass emissions of each individual GHG pollutant by its respective GWP.
(6) The sum of potential annual GHG emissions on a mass basis (i.e., no GWP applied).
(7) The sum of potential annual GHG emissions on a CO2e basis.
Hazardous Air Pollutants
Pollutant | Emission Factor (lb/MMBtu)(1), (2) | Emissions (lb/hr) | Emissions (tons/yr) | Emissions (mg/min)(3) | Emissions (mg/m3)(4)
Acetaldehyde | 2.52e-05 | 0.00048686 | 2.4343e-05 | 3.6806 | 0.0084982
Acrolein | 7.88e-06 | 0.00015224 | 7.6121e-06 | 1.1509 | 0.0026574
Benzene | 0.000776 | 0.014992 | 0.00074962 | 113.3399 | 0.26169
Formaldehyde | 7.89e-05 | 0.0015243 | 7.6217e-05 | 11.5239 | 0.026607
Naphthalene | 0.00013 | 0.0025116 | 0.00012558 | 18.9874 | 0.04384
POM | 0.000212 | 0.0040958 | 0.00020479 | 30.964 | 0.071493
Toluene | 0.000281 | 0.0054289 | 0.00027145 | 41.0419 | 0.094762
Xylenes | 0.000193 | 0.0037288 | 0.00018644 | 28.1889 | 0.065085
(1) Emission factors obtained from AP-42, Ch. 3.4, Tables 3.4-3 and 3.4-4. Emission factors were not included for pollutants at or below the method detection limits, designated as "less than (<)" in AP-42 emission factor tables.
(2) Polycyclic Organic Matter (listed as "Total PAH" in AP-42)
(3) Grams per Pound Conversion Factor | 453.592
(4) Based on stack exhaust flow rate of (ACFM) | 15295

## Fire Water Pump
ESC Brooke County Power I, LLC
Emission Calculations - Fire Water Pump (Tier 2)
Parameter | Value
Heating Value of ULSD (Btu/gal): | 140000
ULSD Sulfur Content (wt. %): | 0.0015
Rated Output (hp): | 315
Fuel Consumption (gal/hr): | 15
Heat Input (MMBtu/hr): | 2.1
Maximum Annual Operation (hr/yr): | 100
NOx + NMHC Emission Factor (g/hp-hr) | 3
Concentration of NOx | 90%
Concentration of NMHC | 10%
Conversion Factor SO2 to SO3 | 10%
Conversion Factor SO3 to H2SO4 | 100%
Molecular weight of S | 32
Molecular weight of SO2 | 64
Molecular weight of SO3 | 80
Molecular weight of H2SO4 | 98
Fuel Oil Density (lb/gal) | 7.05
kg-lb Conversion Factor | 2.2046
CO2 Emission Factor (kg/MMBtu) | 73.96
CO2 Emission Factor (lb/MMBtu) | 163.0537
CH4 Emission Factor (kg/MMBtu) | 0.003
CH4 Emission Factor (lb/MMBtu) | 0.0066139
N2O Emission Factor (kg/MMBtu) | 0.0006
N2O Emission Factor (lb/MMBtu) | 0.0013228
Global Warming Potential - CO2 | 1
Global Warming Potential - CH4 | 25
Global Warming Potential - N2O | 298
Criteria Pollutants
Pollutant | Emission Factor (g/hp-hr)(1) | Emission Factor (lb/MMBtu) | Emissions (lb/hr) | Emissions (tons/yr) | Emissions (mg/min) | Emissions (mg/m3)
VOC | 0.083 | -- | 0.05764 | 0.002882 | 435.7519 | 10.9917
NOx | 2.69 | -- | 1.8681 | 0.093405 | 14122.5623 | 356.2383
CO | 0.44 | -- | 0.30556 | 0.015278 | 2310.0102 | 58.2695
SO2 | -- | 0.0015107 | 0.0031725 | 0.00015862 | 23.9837 | 0.60498
PM/PM10/PM2.5 | 0.0745 | -- | 0.051737 | 0.0025869 | 391.1267 | 9.8661
H2SO4(4) | -- | 0.00023133 | 0.00048579 | 7.2868e-07 | 3.6725 | 0.092638
CO2 | -- | 163.0537 | 342.4128 | 17.1206 | 2588594.81 | 65296.6879
CH4 | -- | 0.0066139 | 0.013889 | 0.00069446 | 104.9998 | 2.6486
N2O | -- | 0.0013228 | 0.0027778 | 0.00013889 | 21 | 0.52972
GHG (Mass Basis) | -- | -- | 342.4294 | 17.1215 | 2588720.8097 | 65299.8662
GHG (CO2e Basis) | -- | -- | 343.5878 | 17.1794 | 2597477.7922 | 65520.759
(1) Emission factors NOx, CO, PM, and VOC provided by vendor. SO2 lb/hr emission rate calculated as a mass balance and based on fuel consumption and fuel oil sulfur content.
(2) Default emission factors obtained from 40 CFR Part 98, Subpart C: General Stationary Fuel Combustion Sources, Tables C-1 and C-2 for distillate fuel oil No. 2 firing.
(3) Global warming potentials (GWP) of each pollutant established by 40 CFR Part 98, Subpart A: General Provisions, Table A-1.
(4) For each GHG, emissions are normalized to a CO2e basis by multiplying the mass emissions of each individual GHG pollutant by its respective GWP.
(5) The sum of potential annual GHG emissions on a mass basis (i.e., no GWP applied).
(6) The sum of potential annual GHG emissions on a CO2e basis.
Hazardous Air Pollutants
Pollutant | Emission Factor (lb/MMBtu)(1), (2) | Emissions (lb/hr) | Emissions (tons/yr) | Emissions (mg/min)(3) | Emissions (mg/m3)(4)
Acetaldehyde | 0.000767 | 0.0016107 | 8.0535e-05 | 12.1767 | 0.30715
Acrolein | 7.88e-06 | 0.000788 | 1.182e-06 | 18.3867 | 0.042453
Benzene | 0.000933 | 0.0019593 | 9.7965e-05 | 14.812 | 0.37363
Formaldehyde | 0.00118 | 0.002478 | 0.0001239 | 18.7333 | 0.47254
Naphthalene | 8.48e-05 | 0.00017808 | 8.904e-06 | 1.3463 | 0.033959
POM | 0.000168 | 0.0003528 | 1.764e-05 | 2.6671 | 0.067277
Toluene | 0.000409 | 0.0008589 | 4.2945e-05 | 6.4932 | 0.16379
Xylenes | 0.000285 | 0.0005985 | 2.9925e-05 | 4.5246 | 0.11413
(1) Emission factors obtained from AP-42, Ch. 3.3, Table 3.3-2. Emission factors were not included for pollutants at or below the method detection limits, designated as "less than (<)" in AP-42 emission factor tables.
(2) Polycyclic Organic Matter (listed as "Total PAH" in AP-42)
(3) Grams per Pound Conversion Factor | 453.592
(4) Based on stack exhaust flow rate of (ACFM) | 1400

## Circuit Breakers SF6
ESC Brooke County Power I, LLC
Emission Calculations - GHGs (SF6) from Circuit Breakers
Pollutant | Emission Source | Count (Breakers) | Mass of SF6 per Breaker (lb/Breaker/year) | Annual SF6 Leak Rate (% by weight) | SF6 Mass Emissions (tons/yr) | Global Warming Potential | CO2e (tons/yr)
SF6 | Generator Breakers | 2 | 25 | 0.5% | 0.000125 | 22800 | 2.85
SF6 | Switchyard Circuit Breakers | 3 | 325 | 0.5% | 0.0024375 | 22800 | 55.575
Total |  | 5 | 350 |  | 0.0025625 |  | 58.425
(1)The annual mass emissions of SF6 from electrical breakers are calculated using the number of breakers, mass of SF6 per breaker, and annual leak rate as follows:
SF6 for Breakers (tons/yr) = Number of Breakers x Mass of SF6 per Breaker (lb) x Annual SF6 Leak Rate (%) x 1 ton/2000 lb
(2) The Global Warming Potential factor for SF6 was obtained from 40 CFR Part 98, Subpart A, Table A-1.

## Stack Parameters
Rev I Combustion Turbines (2) Based on -20°F, 100% DF, evap cooling off, and 100% Natural gas fuel (Case number 1).
Exhaust Flow | 1324466.6667 | acfm
Stack Diameter | 20.5 | ft.
Exit Velocity | 66.8794 | ft/sec
Stack Height | 185 | ft.
Exit Temp. | 164.9 | °F
Auxiliary Boiler
Exhaust Flow | 19925 | acfm
Stack Diameter | 32 | in.
Stack Diameter | 2.6667 | ft.
Exit Velocity | 59.4593 | ft/sec
Stack Height | 65 | ft.
Exit Temp. | 260 | °F
Fuel Gas Heaters (2)
Exhaust Flow | 961 | acfm
Stack Diameter | 7 | in.
Stack Diameter | 0.58333 | ft.
Exit Velocity | 59.9306 | ft/sec
Stack Height | 15 | ft.
Exit Temp. | 600 | °F
Emergency Generator
Exhaust Flow | 15295 | acfm
Stack Diameter | 8 | in
Stack Diameter | 0.66667 | ft.
Exit Velocity | 730.2825 | ft/sec
Stack Height | 30 | ft.
Exit Temp. | 752 | °F
Fire Water Pump
Exhaust Flow | 1400 | acfm
Stack Diameter | 6 | in
Stack Diameter | 0.5 | ft.
Exit Velocity | 118.8357 | ft/sec
Stack Height | 15 | ft.
Exit Temp. | 961 | °F

## BROOKE_RevI_T218_042417
Combined Cycle Systems Emissions Estimates: ESC Brooke County
Operating Point |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126
|  |  | GT Fuel/ DB Fuel = NG/NG ==> | [30 empty] | Wet Gas/Wet Gas ==> | [30 empty] | 50%C2/50%C2 ==> | [30 empty] | Wet Gas/NG ==> | [10 empty] | 50%C2/NG ==> | [10 empty] | 50% C2 / 100 % C2 ==>
Case Description |  |  | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load. | Natural gas, base load.
|  |  | Extreme Cold - 2x100% | Extreme Cold - 2x100% | Extreme Cold - 2x75% | Extreme Cold - 1xMECL | Winter - 2x100% | Winter - 2x100% | Winter - 2x75% | Winter - 1x30% | Average Day - 2x100% | Average Day - 2x100% | Average Day - 2x75% | Average Day - 1x30% | ISO - 2x100% | ISO - 2x100% | ISO - 2x100% | ISO - 1x30% | Summer, Evap Cooling - 2x100% | Summer, Evap Cooling - 2x100% | Summer - 2x100% | Summer - 2x75% | Summer - 1xMECL | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot - 2x100% | Extreme Hot - 2x75% | Extreme Hot - 1xMECL | Extreme Cold - 1x100% | Extreme Cold - 1x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Cold - 2x100% | Extreme Cold - 2x100% | Extreme Cold - 2x75% | Extreme Cold - 1xMECL | Winter - 2x100% | Winter - 2x100% | Winter - 2x75% | Winter - 1x30% | Average Day - 2x100% | Average Day - 2x100% | Average Day - 2x75% | Average Day - 1x30% | ISO - 2x100% | ISO - 2x100% | ISO - 2x100% | ISO - 1x30% | Summer, Evap Cooling - 2x100% | Summer, Evap Cooling - 2x100% | Summer - 2x100% | Summer - 2x75% | Summer - 1xMECL | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot - 2x100% | Extreme Hot - 2x75% | Extreme Hot - 1xMECL | Extreme Cold - 1x100% | Extreme Cold - 1x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Cold - 2x100% | Extreme Cold - 2x100% | Extreme Cold - 2x75% | Extreme Cold - 1xMECL | Winter - 2x100% | Winter - 2x100% | Winter - 2x75% | Winter - 1x30% | Average Day - 2x100% | Average Day - 2x100% | Average Day - 2x75% | Average Day - 1x30% | ISO - 2x100% | ISO - 2x100% | ISO - 2x100% | ISO - 1x30% | Summer, Evap Cooling - 2x100% | Summer, Evap Cooling - 2x100% | Summer - 2x100% | Summer - 2x75% | Summer - 1xMECL | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot - 2x100% | Extreme Hot - 2x75% | Extreme Hot - 1xMECL | Extreme Cold - 1x100% | Extreme Cold - 1x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Cold - 2x100% | Winter - 2x100% | Average Day - 2x100% | ISO - 2x100% | Summer, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Cold - 1x100% | Extreme Cold - 1x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Cold - 2x100% | Winter - 2x100% | Average Day - 2x100% | ISO - 2x100% | Summer, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Cold - 1x100% | Extreme Cold - 1x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Cold - 2x100% | Winter - 2x100% | Average Day - 2x100% | ISO - 2x100% | Summer, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Cold - 1x100% | Extreme Cold - 1x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100% | Extreme Hot, Evap Cooling - 2x100%
|  |  | Fired to Max DB Heat Consumption |  |  |  | Fired to Max DB Heat Consumption |  |  |  | Fired to Max DB Heat Consumption |  |  |  | Fired to Max DB Heat Consumption |  |  |  | Fired to 830MW net plant |  |  |  |  | Fired to Max DB Heat Consumption |  |  |  |  | Fired to Max DB Heat Consumption | Fired 10% DB Turndown limit | 1GT | Fired to 830MW net plant | Fired 10% DB Turndown limit | Fired to Max DB Heat Consumption |  |  |  | Fired to Max DB Heat Consumption |  |  |  | Fired to Max DB Heat Consumption |  |  |  | Fired to Max DB Heat Consumption |  |  |  | Fired to 830MW net plant |  |  |  |  | Fired to Max DB Heat Consumption |  |  |  |  | Fired to Max DB Heat Consumption | Fired 10% DB Turndown limit | 1GT | Fired to 830MW net plant | Fired 10% DB Turndown limit | Fired to Max DB Heat Consumption |  |  |  | Fired to Max DB Heat Consumption |  |  |  | Fired to Max DB Heat Consumption |  |  |  | Fired to Max DB Heat Consumption |  |  |  | Fired to 830MW net plant |  |  |  |  | Fired to Max DB Heat Consumption |  |  |  |  | Fired to Max DB Heat Consumption | Fired 10% DB Turndown limit | 1GT | Fired to 830MW net plant | Fired 10% DB Turndown limit | Fired to Max DB Heat Consumption | Fired to Max DB Heat Consumption | Fired to Max DB Heat Consumption | Fired to Max DB Heat Consumption | Fired to 830MW net plant | Fired to Max DB Heat Consumption | Fired to Max DB Heat Consumption | Fired to Max DB Heat Consumption | 1GT | Fired to 830MW net plant | 1GT | Fired to Max DB Heat Consumption | Fired to Max DB Heat Consumption | Fired to Max DB Heat Consumption | Fired to Max DB Heat Consumption | Fired to 830MW net plant | Fired to Max DB Heat Consumption | Fired to Max DB Heat Consumption | Fired to Max DB Heat Consumption | 1GT | Fired to 830MW net plant | 1GT | Fired to Max DB Heat Consumption | Fired to Max DB Heat Consumption | Fired to Max DB Heat Consumption | Fired to Max DB Heat Consumption | Fired to 830MW net plant | Fired to Max DB Heat Consumption | Fired to Max DB Heat Consumption | Fired to Max DB Heat Consumption | 1GT | Fired to 830MW net plant | 1GT
Ambient Conditions
Ambient Temperature | °F |  | -20 | -20 | -20 | -20 | 32 | 32 | 32 | 32 | 52.4 | 52.4 | 52.4 | 52.4 | 59 | 59 | 59 | 59 | 92 | 92 | 92 | 92 | 92 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | -20 | -20 | 100.3 | 100.3 | 100.3 | -20 | -20 | -20 | -20 | 32 | 32 | 32 | 32 | 52.4 | 52.4 | 52.4 | 52.4 | 59 | 59 | 59 | 59 | 92 | 92 | 92 | 92 | 92 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | -20 | -20 | 100.3 | 100.3 | 100.3 | -20 | -20 | -20 | -20 | 32 | 32 | 32 | 32 | 52.4 | 52.4 | 52.4 | 52.4 | 59 | 59 | 59 | 59 | 92 | 92 | 92 | 92 | 92 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | -20 | -20 | 100.3 | 100.3 | 100.3 | -20 | 32 | 52.4 | 59 | 92 | 100.3 | -20 | -20 | 100.3 | 100.3 | 100.3 | -20 | 32 | 52.4 | 59 | 92 | 100.3 | -20 | -20 | 100.3 | 100.3 | 100.3 | -20 | 32 | 52.4 | 59 | 92 | 100.3 | -20 | -20 | 100.3 | 100.3 | 100.3
Ambient Pressure | psia |  | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072 | 14.072
Ambient Relative Humidity | % |  | 80 | 80 | 80 | 80 | 60 | 60 | 60 | 60 | 70.2 | 70.2 | 70.2 | 70.2 | 60 | 60 | 60 | 60 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 80 | 80 | 45 | 45 | 45 | 80 | 80 | 80 | 80 | 60 | 60 | 60 | 60 | 70.2 | 70.2 | 70.2 | 70.2 | 60 | 60 | 60 | 60 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 80 | 80 | 45 | 45 | 45 | 80 | 80 | 80 | 80 | 60 | 60 | 60 | 60 | 70.2 | 70.2 | 70.2 | 70.2 | 60 | 60 | 60 | 60 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 80 | 80 | 45 | 45 | 45 | 80 | 60 | 70.2 | 60 | 45 | 45 | 80 | 80 | 45 | 45 | 45 | 80 | 60 | 70.2 | 60 | 45 | 45 | 80 | 80 | 45 | 45 | 45 | 80 | 60 | 70.2 | 60 | 45 | 45 | 80 | 80 | 45 | 45 | 45
Gas Turbine
GT fuel type |  |  | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas
Number of Gas Turbines operating per Block |  |  | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1
GT load fraction | % |  | 100 | 100 | 75 | 58 | 100 | 100 | 75 | 40 | 100 | 100 | 75 | 40 | 100 | 100 | 75 | 40 | 100 | 100 | 100 | 75 | 48 | 100 | 100 | 100 | 75 | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 75 | 58 | 100 | 100 | 75 | 40 | 100 | 100 | 75 | 40 | 100 | 100 | 75 | 40 | 100 | 100 | 100 | 75 | 48 | 100 | 100 | 100 | 75 | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 75 | 58 | 100 | 100 | 75 | 40 | 100 | 100 | 75 | 40 | 100 | 100 | 75 | 40 | 100 | 100 | 100 | 75 | 48 | 100 | 100 | 100 | 75 | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Evap Cooler status |  |  | off | off | off | off | off | off | off | off | off | off | off | off | off | off | off | off | ON | ON | off | off | off | ON | ON | off | off | off | off | off | ON | off | ON | off | off | off | off | off | off | off | off | off | off | off | off | off | off | off | off | ON | ON | off | off | off | ON | ON | off | off | off | off | off | ON | off | ON | off | off | off | off | off | off | off | off | off | off | off | off | off | off | off | off | ON | ON | off | off | off | ON | ON | off | off | off | off | off | ON | off | ON | off | off | off | off | ON | ON | off | off | ON | off | ON | off | off | off | off | ON | ON | off | off | ON | off | ON | off | off | off | off | ON | ON | off | off | ON | off | ON
Gas turbine liquid flow | klb/h |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas Turbine Fuel Molar Weight | lb/lbmole |  | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34
Duct Burner Fuel Molar Weight | lb/lbmole |  | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 30.07 | 30.07 | 30.07 | 30.07 | 30.07 | 30.07 | 30.07 | 30.07 | 30.07 | 30.07 | 30.07
Abatement Status
CO Catalyst Operating status |  |  | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating
SCR Operating status |  |  | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating
GT Fuel
Gas Turbine fuel LHV | Btu/lb |  | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694
Gas Turbine fuel HHV | Btu/lb |  | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728
Gas Turbine fuel molecular weight | lb/lbmole |  | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34
Gas Turbine sulfur ppm (by mass) | ppm |  | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3
Duct Burner
Duct Burner fuel LHV | Btu/lb |  | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20786 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 20694 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 21089 | 20431 | 20431 | 20431 | 20431 | 20431 | 20431 | 20431 | 20431 | 20431 | 20431 | 20431
Duct Burner fuel HHV | Btu/lb |  | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22909 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 22728 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 23340 | 22318 | 22318 | 22318 | 22318 | 22318 | 22318 | 22318 | 22318 | 22318 | 22318 | 22318
Duct Burner sulfur ppm (by mass) | ppm |  | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 7.2 | 7.2 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2
Duct Burner status |  |  | Operating | Off | Off | Off | Operating | Off | Off | Off | Operating | Off | Off | Off | Operating | Off | Off | Off | Operating | Off | Off | Off | Off | Operating | Off | Off | Off | Off | Operating | Operating | Operating | Operating | Operating | Operating | Off | Off | Off | Operating | Off | Off | Off | Operating | Off | Off | Off | Operating | Off | Off | Off | Operating | Off | Off | Off | Off | Operating | Off | Off | Off | Off | Operating | Operating | Operating | Operating | Operating | Operating | Off | Off | Off | Operating | Off | Off | Off | Operating | Off | Off | Off | Operating | Off | Off | Off | Operating | Off | Off | Off | Off | Operating | Off | Off | Off | Off | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating | Operating
Duct Burner fuel flow | klb/h |  | 18.2 | 0 | 0 | 0 | 17.3 | 0 | 0 | 0 | 17.1 | 0 | 0 | 0 | 17.4 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18.2 | 0 | 0 | 0 | 0 | 18.2 | 1.8 | 18.2 | 18.2 | 1.8 | 18.4 | 0 | 0 | 0 | 17.3 | 0 | 0 | 0 | 17.1 | 0 | 0 | 0 | 17.4 | 0 | 0 | 0 | 18.4 | 0 | 0 | 0 | 0 | 18.4 | 0 | 0 | 0 | 0 | 18.4 | 1.8 | 18.4 | 18.4 | 1.8 | 18.5 | 0 | 0 | 0 | 17.3 | 0 | 0 | 0 | 17.1 | 0 | 0 | 0 | 17.4 | 0 | 0 | 0 | 18.5 | 0 | 0 | 0 | 0 | 18.5 | 0 | 0 | 0 | 0 | 18.5 | 1.9 | 18.5 | 18.5 | 1.9 | 18.2 | 17.3 | 17.1 | 17.4 | 18.2 | 18.2 | 18.2 | 1.8 | 18.2 | 18.2 | 1.8 | 18.2 | 17.3 | 17.1 | 17.4 | 18.2 | 18.2 | 18.2 | 1.8 | 18.2 | 18.2 | 1.8 | 18.2 | 17.3 | 17.1 | 17.4 | 18.2 | 18.2 | 18.2 | 1.9 | 18.2 | 18.2 | 1.9
Duct Burner load fraction | % |  | 100 | 0 | 0 | 0 | 95.2 | 0 | 0 | 0 | 93.9 | 0 | 0 | 0 | 95.8 | 0 | 0 | 0 | 99.3 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 100 | 10 | 100 | 100 | 10 | 99.6 | 0 | 0 | 0 | 93.5 | 0 | 0 | 0 | 92.2 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 99.6 | 0 | 0 | 0 | 0 | 99.6 | 0 | 0 | 0 | 0 | 99.6 | 10 | 99.6 | 99.6 | 10 | 99.2 | 0 | 0 | 0 | 92.7 | 0 | 0 | 0 | 91.5 | 0 | 0 | 0 | 93.2 | 0 | 0 | 0 | 99.2 | 0 | 0 | 0 | 0 | 99.2 | 0 | 0 | 0 | 0 | 99.2 | 10 | 99.2 | 99.2 | 10 | 100 | 95.2 | 93.9 | 95.8 | 100 | 100 | 100 | 10 | 100 | 100 | 10 | 100 | 95.2 | 93.9 | 95.8 | 100 | 100 | 100 | 10 | 100 | 100 | 10 | 95.6 | 91 | 89.8 | 91.6 | 95.6 | 95.6 | 95.6 | 10 | 95.6 | 95.6 | 10
Duct Burner Fuel Molar Weight | lb/lbmole |  | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 20.42 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 23.34 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 17.54 | 30.07 | 30.07 | 30.07 | 30.07 | 30.07 | 30.07 | 30.07 | 30.07 | 30.07 | 30.07 | 30.07
Heat Consumption for permitting (per unit)
GT Heat Cons (HHV), with permitting margin | MMBtu/h |  | 2735 | 2735 | 2184.4 | 1852.2 | 2722.7 | 2722.7 | 2148 | 1418.5 | 2696.9 | 2696.9 | 2117.9 | 1393.5 | 2657 | 2657 | 2091.3 | 1377.2 | 2571.5 | 2571.5 | 2470.7 | 1951.3 | 1444.1 | 2536.1 | 2536.1 | 2390.8 | 1893.9 | 1441.6 | 2736.8 | 2737.7 | 2537.8 | 2392.7 | 2538.7 | 2719.7 | 2719.7 | 2172.2 | 1842.4 | 2707.2 | 2707.2 | 2135.8 | 1411 | 2679 | 2679 | 2104.8 | 1385.4 | 2639.4 | 2639.4 | 2078.4 | 1369.2 | 2554.5 | 2554.5 | 2454.4 | 1939.1 | 1435.5 | 2519.4 | 2519.4 | 2375.1 | 1882 | 1432.9 | 2721.5 | 2722.3 | 2521.1 | 2377 | 2521.9 | 2700.8 | 2700.8 | 2170.1 | 1846.5 | 2690.1 | 2690.1 | 2135.9 | 1421.1 | 2663.9 | 2663.9 | 2105.6 | 1396.2 | 2624.5 | 2624.5 | 2079.8 | 1380.3 | 2540.2 | 2540.2 | 2440.7 | 1940.1 | 1444.5 | 2505.2 | 2505.2 | 2361.8 | 1872 | 1425.6 | 2702.6 | 2703.4 | 2506.9 | 2363.7 | 2507.7 | 2719.7 | 2707.2 | 2679 | 2639.4 | 2554.5 | 2519.4 | 2721.5 | 2722.3 | 2521.1 | 2377 | 2521.9 | 2700.8 | 2690.1 | 2663.9 | 2624.5 | 2540.2 | 2505.2 | 2702.6 | 2703.4 | 2506.9 | 2363.7 | 2507.7 | 2700.8 | 2690.1 | 2663.9 | 2624.5 | 2540.2 | 2505.2 | 2702.6 | 2703.4 | 2507 | 2363.7 | 2507.7
DB Heat Cons (HHV) | MMBtu/h |  | 424.1 | 0 | 0 | 0 | 403.8 | 0 | 0 | 0 | 398.4 | 0 | 0 | 0 | 406.1 | 0 | 0 | 0 | 421.1 | 0 | 0 | 0 | 0 | 424.1 | 0 | 0 | 0 | 0 | 424.1 | 42.4 | 424.1 | 424.1 | 42.4 | 422.3 | 0 | 0 | 0 | 396.4 | 0 | 0 | 0 | 391.1 | 0 | 0 | 0 | 398.6 | 0 | 0 | 0 | 422.3 | 0 | 0 | 0 | 0 | 422.3 | 0 | 0 | 0 | 0 | 422.3 | 42.2 | 422.3 | 422.3 | 42.2 | 420.9 | 0 | 0 | 0 | 393.2 | 0 | 0 | 0 | 388 | 0 | 0 | 0 | 395.5 | 0 | 0 | 0 | 420.9 | 0 | 0 | 0 | 0 | 420.9 | 0 | 0 | 0 | 0 | 420.9 | 42.4 | 420.9 | 420.9 | 42.4 | 424.1 | 403.8 | 398.4 | 406.1 | 424.1 | 424.1 | 424.1 | 42.4 | 424.1 | 424.1 | 42.4 | 424.1 | 403.8 | 398.4 | 406.1 | 424.1 | 424.1 | 424.1 | 42.4 | 424.1 | 424.1 | 42.4 | 405.5 | 386.1 | 381 | 388.4 | 405.5 | 405.5 | 405.5 | 42.4 | 405.5 | 405.5 | 42.4
HRSG Exit Exhaust gas (per unit)
Stack N2 mole fraction | - |  | 0.74 | 0.75 | 0.75 | 0.75 | 0.74 | 0.75 | 0.75 | 0.75 | 0.74 | 0.74 | 0.74 | 0.75 | 0.74 | 0.74 | 0.74 | 0.75 | 0.72 | 0.73 | 0.73 | 0.73 | 0.74 | 0.72 | 0.72 | 0.73 | 0.73 | 0.73 | 0.74 | 0.75 | 0.72 | 0.72 | 0.72 | 0.75 | 0.75 | 0.75 | 0.75 | 0.74 | 0.75 | 0.75 | 0.75 | 0.74 | 0.74 | 0.74 | 0.75 | 0.74 | 0.74 | 0.74 | 0.75 | 0.72 | 0.73 | 0.73 | 0.73 | 0.74 | 0.72 | 0.72 | 0.73 | 0.73 | 0.73 | 0.75 | 0.75 | 0.72 | 0.72 | 0.72 | 0.75 | 0.75 | 0.75 | 0.75 | 0.74 | 0.75 | 0.75 | 0.75 | 0.74 | 0.74 | 0.75 | 0.75 | 0.74 | 0.74 | 0.74 | 0.75 | 0.73 | 0.73 | 0.73 | 0.74 | 0.74 | 0.72 | 0.72 | 0.73 | 0.73 | 0.73 | 0.75 | 0.75 | 0.72 | 0.72 | 0.72 | 0.75 | 0.74 | 0.74 | 0.74 | 0.72 | 0.72 | 0.75 | 0.75 | 0.72 | 0.72 | 0.72 | 0.75 | 0.74 | 0.74 | 0.74 | 0.73 | 0.72 | 0.75 | 0.75 | 0.72 | 0.72 | 0.72 | 0.75 | 0.74 | 0.74 | 0.74 | 0.73 | 0.72 | 0.75 | 0.75 | 0.72 | 0.73 | 0.72
Stack O2 mole fraction | - |  | 0.1 | 0.12 | 0.12 | 0.12 | 0.1 | 0.12 | 0.12 | 0.13 | 0.1 | 0.12 | 0.12 | 0.13 | 0.1 | 0.12 | 0.12 | 0.13 | 0.1 | 0.11 | 0.12 | 0.12 | 0.13 | 0.1 | 0.11 | 0.11 | 0.12 | 0.12 | 0.1 | 0.12 | 0.1 | 0.1 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.1 | 0.12 | 0.12 | 0.13 | 0.1 | 0.12 | 0.12 | 0.13 | 0.1 | 0.12 | 0.12 | 0.13 | 0.1 | 0.11 | 0.12 | 0.12 | 0.13 | 0.1 | 0.11 | 0.12 | 0.12 | 0.13 | 0.11 | 0.12 | 0.1 | 0.1 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.11 | 0.12 | 0.12 | 0.13 | 0.1 | 0.12 | 0.12 | 0.13 | 0.1 | 0.12 | 0.12 | 0.13 | 0.1 | 0.11 | 0.12 | 0.12 | 0.13 | 0.1 | 0.11 | 0.12 | 0.12 | 0.13 | 0.11 | 0.12 | 0.1 | 0.1 | 0.11 | 0.11 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.11 | 0.12 | 0.1 | 0.1 | 0.11 | 0.11 | 0.11 | 0.1 | 0.1 | 0.1 | 0.1 | 0.11 | 0.12 | 0.1 | 0.1 | 0.11 | 0.11 | 0.11 | 0.1 | 0.1 | 0.1 | 0.1 | 0.11 | 0.12 | 0.1 | 0.1 | 0.11
Stack AR mole fraction | - |  | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Stack H2O mole fraction | - |  | 0.09 | 0.08 | 0.08 | 0.08 | 0.1 | 0.08 | 0.08 | 0.08 | 0.1 | 0.09 | 0.09 | 0.08 | 0.1 | 0.09 | 0.09 | 0.08 | 0.12 | 0.11 | 0.1 | 0.1 | 0.09 | 0.13 | 0.11 | 0.11 | 0.1 | 0.1 | 0.09 | 0.08 | 0.13 | 0.12 | 0.12 | 0.09 | 0.08 | 0.08 | 0.08 | 0.09 | 0.08 | 0.08 | 0.07 | 0.1 | 0.09 | 0.09 | 0.08 | 0.1 | 0.09 | 0.09 | 0.08 | 0.12 | 0.1 | 0.1 | 0.1 | 0.09 | 0.12 | 0.11 | 0.1 | 0.1 | 0.1 | 0.09 | 0.08 | 0.12 | 0.12 | 0.11 | 0.09 | 0.07 | 0.07 | 0.07 | 0.09 | 0.08 | 0.08 | 0.07 | 0.09 | 0.08 | 0.08 | 0.07 | 0.1 | 0.08 | 0.08 | 0.07 | 0.11 | 0.1 | 0.1 | 0.09 | 0.09 | 0.12 | 0.11 | 0.1 | 0.1 | 0.09 | 0.09 | 0.08 | 0.12 | 0.11 | 0.11 | 0.09 | 0.09 | 0.1 | 0.1 | 0.12 | 0.12 | 0.09 | 0.08 | 0.12 | 0.12 | 0.11 | 0.09 | 0.09 | 0.1 | 0.1 | 0.11 | 0.12 | 0.09 | 0.08 | 0.12 | 0.12 | 0.11 | 0.08 | 0.09 | 0.09 | 0.09 | 0.11 | 0.12 | 0.08 | 0.08 | 0.12 | 0.11 | 0.11
Stack CO2 mole fraction | - |  | 0.05 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.05 | 0.05 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.05 | 0.05 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.05 | 0.05 | 0.04 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Stack Molecular Weight | lb/lbmole |  | 28.39 | 28.47 | 28.47 | 28.48 | 28.35 | 28.42 | 28.43 | 28.48 | 28.29 | 28.36 | 28.37 | 28.43 | 28.28 | 28.36 | 28.37 | 28.42 | 28.09 | 28.17 | 28.23 | 28.25 | 28.28 | 28.01 | 28.09 | 28.16 | 28.18 | 28.21 | 28.39 | 28.46 | 28.01 | 28.08 | 28.08 | 28.46 | 28.53 | 28.53 | 28.54 | 28.42 | 28.49 | 28.49 | 28.54 | 28.36 | 28.43 | 28.43 | 28.48 | 28.35 | 28.42 | 28.43 | 28.47 | 28.16 | 28.23 | 28.29 | 28.3 | 28.33 | 28.08 | 28.15 | 28.22 | 28.24 | 28.26 | 28.46 | 28.52 | 28.08 | 28.14 | 28.14 | 28.52 | 28.58 | 28.58 | 28.59 | 28.48 | 28.54 | 28.54 | 28.58 | 28.42 | 28.47 | 28.48 | 28.52 | 28.41 | 28.47 | 28.48 | 28.52 | 28.21 | 28.27 | 28.34 | 28.35 | 28.38 | 28.14 | 28.2 | 28.26 | 28.28 | 28.31 | 28.52 | 28.57 | 28.13 | 28.2 | 28.19 | 28.45 | 28.41 | 28.35 | 28.34 | 28.15 | 28.07 | 28.45 | 28.52 | 28.07 | 28.13 | 28.14 | 28.5 | 28.46 | 28.4 | 28.39 | 28.19 | 28.12 | 28.5 | 28.57 | 28.12 | 28.18 | 28.19 | 28.53 | 28.49 | 28.43 | 28.42 | 28.23 | 28.15 | 28.53 | 28.57 | 28.15 | 28.21 | 28.19
Stack Temperature | °F |  | 164.9 | 187.1 | 179.5 | 173.4 | 163.7 | 183.8 | 176.2 | 172.2 | 169.6 | 183.3 | 175.5 | 172.2 | 171.3 | 185.4 | 175.4 | 172.2 | 193.4 | 201.6 | 199.9 | 190.5 | 176.3 | 199.9 | 206.5 | 203.4 | 195.6 | 180.4 | 164.2 | 183 | 173.5 | 171 | 187.2 | 164.9 | 187.2 | 179.6 | 173.4 | 163.9 | 183.9 | 176.2 | 172.2 | 169.7 | 183.3 | 175.4 | 172.3 | 171.4 | 185.3 | 175.4 | 172.3 | 193.2 | 201.5 | 199.9 | 190.4 | 176.4 | 199.7 | 206.5 | 203.4 | 195.6 | 180.5 | 164.2 | 183 | 173.4 | 170.9 | 187.1 | 164.8 | 187.2 | 179.4 | 173.6 | 163.9 | 183.9 | 176 | 172.5 | 169.6 | 183.3 | 175.7 | 172.5 | 171.3 | 185.3 | 175.6 | 172.5 | 193.2 | 201.5 | 199.8 | 190.9 | 176.7 | 199.7 | 206.5 | 203.4 | 195.7 | 180.5 | 164.2 | 183.1 | 173.3 | 170.8 | 187.2 | 164.9 | 163.7 | 169.6 | 171.3 | 193.3 | 199.7 | 164.2 | 183 | 173.4 | 170.9 | 187.1 | 164.9 | 163.7 | 169.5 | 171.2 | 193.2 | 199.7 | 164.2 | 183.1 | 173.3 | 170.8 | 187.2 | 166.1 | 165 | 170.6 | 172.2 | 193.7 | 200.1 | 165.5 | 183.7 | 174.1 | 171.7 | 187.6
Stack Mass flow, including Permitting Margin, per stack | lb/h |  | 4973500 | 4954500 | 3982800 | 3439300 | 4889100 | 4871000 | 3884700 | 2876300 | 4848500 | 4830600 | 3858000 | 2858800 | 4792300 | 4774000 | 3836100 | 2844300 | 4646100 | 4627200 | 4532600 | 3711600 | 2981500 | 4586200 | 4567200 | 4383800 | 3643500 | 2985600 | 4973400 | 4956200 | 4586300 | 4403000 | 4569200 | 4980800 | 4961500 | 3988300 | 3443300 | 4896000 | 4877800 | 3889800 | 2879400 | 4849900 | 4832000 | 3860200 | 2860900 | 4793700 | 4775500 | 3838300 | 2846400 | 4648000 | 4628600 | 4533900 | 3713600 | 2983200 | 4587900 | 4568600 | 4385200 | 3645300 | 2987300 | 4980700 | 4963200 | 4588000 | 4404600 | 4570600 | 4976200 | 4956700 | 4008100 | 3487100 | 4894700 | 4876600 | 3912800 | 2934200 | 4850200 | 4832300 | 3897900 | 2917000 | 4794000 | 4775700 | 3878300 | 2903800 | 4648400 | 4628900 | 4534300 | 3755400 | 3039700 | 4588300 | 4568900 | 4385500 | 3646100 | 2988300 | 4976000 | 4958500 | 4588400 | 4405000 | 4570900 | 4980600 | 4896000 | 4849900 | 4793700 | 4647700 | 4587600 | 4980400 | 4963200 | 4587700 | 4404300 | 4570600 | 4975800 | 4894700 | 4850200 | 4794000 | 4648000 | 4588000 | 4975700 | 4958400 | 4588000 | 4404700 | 4570900 | 4975800 | 4894700 | 4850200 | 4794000 | 4648000 | 4588000 | 4975700 | 4958500 | 4588000 | 4404700 | 4571000
Stack Volume flow (actual) per stack | Mft³/h |  | 79.468 | 81.758 | 64.944 | 55.526 | 78.082 | 80.09 | 63.103 | 46.342 | 78.331 | 79.534 | 62.725 | 46.156 | 77.658 | 78.871 | 62.375 | 45.932 | 78.462 | 78.899 | 76.916 | 62.045 | 48.696 | 78.431 | 78.673 | 74.976 | 61.536 | 49.199 | 79.384 | 81.285 | 75.296 | 71.834 | 76.441 | 79.385 | 81.706 | 64.904 | 55.478 | 78.018 | 80.034 | 63.057 | 46.307 | 78.162 | 79.381 | 62.628 | 46.105 | 77.49 | 78.721 | 62.279 | 45.881 | 78.283 | 78.749 | 76.771 | 61.95 | 48.636 | 78.25 | 78.523 | 74.835 | 61.442 | 49.139 | 79.302 | 81.231 | 75.124 | 71.672 | 76.296 | 79.149 | 81.497 | 65.1 | 56.109 | 77.848 | 79.887 | 63.296 | 47.134 | 78.011 | 79.254 | 63.153 | 46.955 | 77.341 | 78.595 | 62.843 | 46.754 | 78.126 | 78.619 | 76.643 | 62.593 | 49.51 | 78.095 | 78.398 | 74.718 | 61.363 | 49.088 | 79.069 | 81.022 | 74.975 | 71.531 | 76.173 | 79.412 | 78.024 | 78.177 | 77.506 | 78.309 | 78.276 | 79.327 | 81.233 | 75.149 | 71.696 | 76.298 | 79.198 | 77.87 | 78.045 | 77.375 | 78.176 | 78.145 | 79.117 | 81.03 | 75.023 | 71.578 | 76.179 | 79.276 | 77.942 | 78.091 | 77.414 | 78.146 | 78.1 | 79.188 | 81.1 | 75.028 | 71.585 | 76.219
HRSG Exit Emissions (per unit)
NOx Volume fraction, dry, at 15% O2 | ppm |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
NOx mass flow rate (as NO2) | lb/h |  | 23.1 | 19.9 | 15.9 | 13.5 | 22.9 | 19.8 | 15.6 | 10.3 | 22.7 | 19.6 | 15.4 | 10.1 | 22.4 | 19.3 | 15.2 | 10 | 21.9 | 18.7 | 18 | 14.2 | 10.5 | 21.7 | 18.4 | 17.4 | 13.8 | 10.5 | 23.2 | 20.2 | 21.7 | 20.7 | 18.8 | 23.1 | 19.9 | 15.9 | 13.5 | 22.8 | 19.8 | 15.6 | 10.3 | 22.6 | 19.6 | 15.4 | 10.1 | 22.4 | 19.3 | 15.2 | 10 | 21.9 | 18.7 | 17.9 | 14.2 | 10.5 | 21.7 | 18.4 | 17.4 | 13.7 | 10.5 | 23.1 | 20.2 | 21.7 | 20.6 | 18.8 | 23 | 19.8 | 15.9 | 13.5 | 22.7 | 19.7 | 15.6 | 10.4 | 22.5 | 19.5 | 15.4 | 10.2 | 22.3 | 19.2 | 15.2 | 10.1 | 21.9 | 18.6 | 17.9 | 14.2 | 10.6 | 21.6 | 18.3 | 17.3 | 13.7 | 10.4 | 23 | 20.1 | 21.6 | 20.6 | 18.7 | 23.1 | 22.9 | 22.6 | 22.4 | 21.9 | 21.7 | 23.1 | 20.2 | 21.7 | 20.6 | 18.8 | 23 | 22.8 | 22.6 | 22.3 | 21.9 | 21.6 | 23 | 20.1 | 21.6 | 20.6 | 18.7 | 22.9 | 22.7 | 22.5 | 22.2 | 21.8 | 21.5 | 22.9 | 20.1 | 21.5 | 20.5 | 18.7
CO Volume fraction, dry, at 15% O2 | ppm |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
CO mass flow rate | lb/h |  | 14.1 | 12.1 | 9.7 | 8.2 | 13.9 | 12.1 | 9.5 | 6.3 | 13.8 | 11.9 | 9.4 | 6.2 | 13.7 | 11.8 | 9.3 | 6.1 | 13.4 | 11.4 | 10.9 | 8.6 | 6.4 | 13.2 | 11.2 | 10.6 | 8.4 | 6.4 | 14.1 | 12.3 | 13.2 | 12.6 | 11.4 | 14.1 | 12.1 | 9.7 | 8.2 | 13.9 | 12 | 9.5 | 6.3 | 13.8 | 11.9 | 9.4 | 6.2 | 13.6 | 11.7 | 9.2 | 6.1 | 13.4 | 11.4 | 10.9 | 8.6 | 6.4 | 13.2 | 11.2 | 10.6 | 8.4 | 6.4 | 14.1 | 12.3 | 13.2 | 12.6 | 11.4 | 14 | 12 | 9.7 | 8.2 | 13.8 | 12 | 9.5 | 6.3 | 13.7 | 11.9 | 9.4 | 6.2 | 13.6 | 11.7 | 9.3 | 6.1 | 13.3 | 11.3 | 10.9 | 8.6 | 6.4 | 13.2 | 11.2 | 10.5 | 8.3 | 6.3 | 14 | 12.3 | 13.2 | 12.5 | 11.4 | 14.1 | 13.9 | 13.8 | 13.6 | 13.4 | 13.2 | 14.1 | 12.3 | 13.2 | 12.6 | 11.4 | 14 | 13.9 | 13.7 | 13.6 | 13.3 | 13.2 | 14 | 12.2 | 13.2 | 12.5 | 11.4 | 14 | 13.8 | 13.7 | 13.5 | 13.2 | 13.1 | 14 | 12.3 | 13.1 | 12.5 | 11.4
VOC Volume fraction, dry, at 15% O2 | ppm |  | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
VOC mass flow rate (as methane) | lb/h |  | 8.1 | 3.5 | 2.8 | 2.3 | 8 | 3.5 | 2.7 | 1.8 | 7.9 | 3.4 | 2.7 | 1.8 | 7.8 | 3.4 | 2.7 | 1.7 | 7.6 | 3.3 | 3.1 | 2.5 | 1.8 | 7.6 | 3.2 | 3 | 2.4 | 1.8 | 8.1 | 7.1 | 7.6 | 7.2 | 6.5 | 8.1 | 3.5 | 2.8 | 2.3 | 8 | 3.4 | 2.7 | 1.8 | 7.9 | 3.4 | 2.7 | 1.8 | 7.8 | 3.4 | 2.6 | 1.7 | 7.6 | 3.3 | 3.1 | 2.5 | 1.8 | 7.6 | 3.2 | 3 | 2.4 | 1.8 | 8.1 | 7.1 | 7.6 | 7.2 | 6.5 | 8 | 3.4 | 2.8 | 2.4 | 7.9 | 3.4 | 2.7 | 1.8 | 7.8 | 3.4 | 2.7 | 1.8 | 7.8 | 3.4 | 2.7 | 1.8 | 7.6 | 3.2 | 3.1 | 2.5 | 1.8 | 7.5 | 3.2 | 3 | 2.4 | 1.8 | 8 | 7 | 7.5 | 7.2 | 6.5 | 8.1 | 8 | 7.9 | 7.8 | 7.6 | 7.6 | 8.1 | 7.1 | 7.6 | 7.2 | 6.5 | 8 | 8 | 7.9 | 7.8 | 7.6 | 7.5 | 8 | 7 | 7.5 | 7.2 | 6.5 | 8 | 7.9 | 7.8 | 7.8 | 7.6 | 7.5 | 8 | 7 | 7.5 | 7.1 | 6.5
NH3 Volume fraction, dry, at 15% O2 | ppm |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
NH3 mass flow rate | lb/h |  | 21.4 | 18.4 | 14.7 | 12.5 | 21.2 | 18.3 | 14.5 | 9.5 | 21 | 18.1 | 14.2 | 9.4 | 20.8 | 17.9 | 14.1 | 9.3 | 20.3 | 17.3 | 16.6 | 13.1 | 9.7 | 20.1 | 17.1 | 16.1 | 12.7 | 9.7 | 21.4 | 18.7 | 20.1 | 19.1 | 17.4 | 21.4 | 18.4 | 14.7 | 12.5 | 21.1 | 18.3 | 14.4 | 9.5 | 20.9 | 18.1 | 14.2 | 9.4 | 20.7 | 17.9 | 14.1 | 9.3 | 20.3 | 17.3 | 16.6 | 13.1 | 9.7 | 20.1 | 17 | 16.1 | 12.7 | 9.7 | 21.4 | 18.7 | 20.1 | 19.1 | 17.4 | 21.3 | 18.3 | 14.7 | 12.5 | 21 | 18.2 | 14.5 | 9.6 | 20.8 | 18.1 | 14.3 | 9.5 | 20.6 | 17.8 | 14.1 | 9.3 | 20.2 | 17.2 | 16.5 | 13.1 | 9.8 | 20 | 17 | 16 | 12.7 | 9.7 | 21.3 | 18.6 | 20 | 19 | 17.3 | 21.4 | 21.2 | 21 | 20.7 | 20.3 | 20.1 | 21.4 | 18.7 | 20.1 | 19.1 | 17.4 | 21.3 | 21.1 | 20.9 | 20.7 | 20.2 | 20 | 21.3 | 18.6 | 20 | 19 | 17.3 | 21.2 | 21 | 20.8 | 20.6 | 20.1 | 19.9 | 21.2 | 18.6 | 19.9 | 18.9 | 17.3
SOx mass flow rate (as SO2) | lb/h |  | 4 | 3.5 | 2.8 | 2.4 | 4 | 3.5 | 2.7 | 1.8 | 4 | 3.4 | 2.7 | 1.8 | 3.9 | 3.4 | 2.7 | 1.7 | 3.8 | 3.3 | 3.1 | 2.5 | 1.8 | 3.8 | 3.2 | 3 | 2.4 | 1.8 | 4 | 3.5 | 3.8 | 3.6 | 3.3 | 3.5 | 3 | 2.4 | 2 | 3.5 | 3 | 2.4 | 1.6 | 3.4 | 3 | 2.3 | 1.5 | 3.4 | 2.9 | 2.3 | 1.5 | 3.3 | 2.8 | 2.7 | 2.2 | 1.6 | 3.3 | 2.8 | 2.6 | 2.1 | 1.6 | 3.5 | 3.1 | 3.3 | 3.1 | 2.9 | 3.1 | 2.6 | 2.1 | 1.8 | 3 | 2.6 | 2.1 | 1.4 | 3 | 2.6 | 2.1 | 1.4 | 3 | 2.6 | 2 | 1.4 | 2.9 | 2.5 | 2.4 | 1.9 | 1.4 | 2.9 | 2.5 | 2.3 | 1.8 | 1.4 | 3.1 | 2.7 | 2.9 | 2.8 | 2.5 | 3.6 | 3.5 | 3.5 | 3.5 | 3.4 | 3.4 | 3.6 | 3.1 | 3.4 | 3.2 | 2.9 | 3.2 | 3.2 | 3.1 | 3.1 | 3.1 | 3 | 3.2 | 2.7 | 3 | 2.9 | 2.5 | 3 | 3 | 2.9 | 2.9 | 2.8 | 2.8 | 3 | 2.7 | 2.8 | 2.6 | 2.5
Total Particulates | lb/h |  | 14.1 | 9.49 | 9.07 | 8.82 | 13.8 | 9.48 | 9.04 | 8.49 | 13.8 | 9.46 | 9.02 | 8.47 | 13.8 | 9.43 | 9 | 8.45 | 13.9 | 9.37 | 9.29 | 8.89 | 8.51 | 13.9 | 9.34 | 9.23 | 8.85 | 8.5 | 14.1 | 13.8 | 13.9 | 13.8 | 13.6 | 15.8 | 11.3 | 11 | 10.7 | 15.6 | 11.3 | 10.9 | 10.4 | 15.5 | 11.3 | 10.9 | 10.4 | 15.5 | 11.3 | 10.9 | 10.4 | 15.7 | 11.2 | 11.1 | 10.8 | 10.5 | 15.7 | 11.2 | 11.1 | 10.8 | 10.5 | 15.8 | 15.6 | 15.7 | 15.6 | 15.4 | 16.8 | 12.3 | 12 | 11.8 | 16.5 | 12.3 | 12 | 11.6 | 16.4 | 12.3 | 12 | 11.6 | 16.5 | 12.3 | 12 | 11.6 | 16.7 | 12.3 | 12.2 | 11.9 | 11.6 | 16.7 | 12.2 | 12.1 | 11.9 | 11.6 | 16.8 | 16.6 | 16.7 | 16.6 | 16.5 | 15.9 | 15.7 | 15.6 | 15.7 | 15.8 | 15.8 | 15.9 | 15.6 | 15.8 | 15.7 | 15.5 | 16.9 | 16.7 | 16.6 | 16.7 | 16.8 | 16.8 | 16.9 | 16.6 | 16.8 | 16.7 | 16.5 | 16.6 | 16.4 | 16.3 | 16.4 | 16.5 | 16.5 | 16.6 | 16.6 | 16.5 | 16.4 | 16.5
Sulfur Mist | lb/h |  | 2.6 | 2.2 | 1.8 | 1.5 | 2.6 | 2.2 | 1.8 | 1.2 | 2.5 | 2.2 | 1.7 | 1.1 | 2.5 | 2.2 | 1.7 | 1.1 | 2.5 | 2.1 | 2 | 1.6 | 1.2 | 2.4 | 2.1 | 2 | 1.5 | 1.2 | 2.6 | 2.3 | 2.4 | 2.3 | 2.1 | 2.3 | 1.9 | 1.6 | 1.3 | 2.2 | 1.9 | 1.5 | 1 | 2.2 | 1.9 | 1.5 | 1 | 2.2 | 1.9 | 1.5 | 1 | 2.1 | 1.8 | 1.8 | 1.4 | 1 | 2.1 | 1.8 | 1.7 | 1.3 | 1 | 2.3 | 2 | 2.1 | 2 | 1.8 | 2 | 1.7 | 1.4 | 1.2 | 2 | 1.7 | 1.3 | 0.9 | 1.9 | 1.7 | 1.3 | 0.9 | 1.9 | 1.7 | 1.3 | 0.9 | 1.9 | 1.6 | 1.5 | 1.2 | 0.9 | 1.9 | 1.6 | 1.5 | 1.2 | 0.9 | 2 | 1.7 | 1.9 | 1.8 | 1.6 | 2.3 | 2.3 | 2.3 | 2.2 | 2.2 | 2.2 | 2.3 | 2 | 2.2 | 2.1 | 1.8 | 2.1 | 2 | 2 | 2 | 2 | 1.9 | 2.1 | 1.7 | 1.9 | 1.9 | 1.6 | 1.9 | 1.9 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9 | 1.7 | 1.8 | 1.7 | 1.6
Stack CO2 mass flow rate, including Permitting margin | lb/h |  | 396000 | 340000 | 272000 | 231000 | 391000 | 339000 | 267000 | 177000 | 387000 | 336000 | 264000 | 174000 | 383000 | 331000 | 260000 | 172000 | 375000 | 320000 | 308000 | 243000 | 180000 | 371000 | 316000 | 298000 | 236000 | 180000 | 396000 | 346000 | 371000 | 353000 | 321000 | 408000 | 352000 | 281000 | 238000 | 403000 | 350000 | 276000 | 183000 | 399000 | 346000 | 272000 | 179000 | 395000 | 341000 | 269000 | 177000 | 387000 | 330000 | 317000 | 251000 | 186000 | 383000 | 326000 | 307000 | 243000 | 185000 | 409000 | 358000 | 383000 | 364000 | 332000 | 417000 | 359000 | 288000 | 245000 | 412000 | 357000 | 284000 | 189000 | 407000 | 354000 | 280000 | 186000 | 403000 | 348000 | 276000 | 183000 | 395000 | 337000 | 324000 | 258000 | 192000 | 391000 | 333000 | 314000 | 249000 | 189000 | 417000 | 365000 | 391000 | 372000 | 339000 | 407000 | 402000 | 398000 | 394000 | 385000 | 381000 | 407000 | 357000 | 381000 | 362000 | 331000 | 414000 | 410000 | 405000 | 401000 | 392000 | 388000 | 414000 | 364000 | 388000 | 369000 | 338000 | 417000 | 413000 | 409000 | 405000 | 396000 | 391000 | 417000 | 365000 | 391000 | 372000 | 339000
CH4 | lb/hr |  | 6.9646 | 6.0296 | 4.8158 | 4.0834 | 6.8927 | 6.0025 | 4.7355 | 3.1273 | 6.824 | 5.9456 | 4.6692 | 3.0721 | 6.753 | 5.8577 | 4.6105 | 3.0362 | 6.5975 | 5.6692 | 5.447 | 4.3019 | 3.1837 | 6.5261 | 5.5911 | 5.2708 | 4.1753 | 3.1782 | 6.9686 | 6.1291 | 6.5299 | 6.21 | 5.6903 | 6.9269 | 5.9959 | 4.7889 | 4.0618 | 6.8423 | 5.9683 | 4.7086 | 3.1107 | 6.7684 | 5.9062 | 4.6403 | 3.0543 | 6.6976 | 5.8189 | 4.5821 | 3.0186 | 6.5627 | 5.6317 | 5.411 | 4.275 | 3.1647 | 6.4853 | 5.5543 | 5.2362 | 4.1491 | 3.159 | 6.9309 | 6.0947 | 6.4891 | 6.1714 | 5.6529 | 6.8822 | 5.9542 | 4.7842 | 4.0708 | 6.7975 | 5.9306 | 4.7088 | 3.133 | 6.7283 | 5.8729 | 4.642 | 3.0781 | 6.658 | 5.786 | 4.5852 | 3.043 | 6.5281 | 5.6002 | 5.3808 | 4.2772 | 3.1846 | 6.4509 | 5.523 | 5.2069 | 4.127 | 3.1429 | 6.8861 | 6.0534 | 6.4547 | 6.139 | 5.622 | 6.9309 | 6.8586 | 6.7845 | 6.7142 | 6.5667 | 6.4893 | 6.9349 | 6.0951 | 6.493 | 6.1754 | 5.6533 | 6.8892 | 6.8209 | 6.7512 | 6.6813 | 6.5352 | 6.458 | 6.8932 | 6.0534 | 6.4617 | 6.146 | 5.622 | 6.8482 | 6.7819 | 6.7128 | 6.6423 | 6.4941 | 6.417 | 6.8522 | 6.0534 | 6.421 | 6.105 | 5.622
N2O | lb/hr |  | 0.69646 | 0.60296 | 0.48158 | 0.40834 | 0.68927 | 0.60025 | 0.47355 | 0.31273 | 0.6824 | 0.59456 | 0.46692 | 0.30721 | 0.6753 | 0.58577 | 0.46105 | 0.30362 | 0.65975 | 0.56692 | 0.5447 | 0.43019 | 0.31837 | 0.65261 | 0.55911 | 0.52708 | 0.41753 | 0.31782 | 0.69686 | 0.61291 | 0.65299 | 0.621 | 0.56903 | 0.69269 | 0.59959 | 0.47889 | 0.40618 | 0.68423 | 0.59683 | 0.47086 | 0.31107 | 0.67684 | 0.59062 | 0.46403 | 0.30543 | 0.66976 | 0.58189 | 0.45821 | 0.30186 | 0.65627 | 0.56317 | 0.5411 | 0.4275 | 0.31647 | 0.64853 | 0.55543 | 0.52362 | 0.41491 | 0.3159 | 0.69309 | 0.60947 | 0.64891 | 0.61714 | 0.56529 | 0.68822 | 0.59542 | 0.47842 | 0.40708 | 0.67975 | 0.59306 | 0.47088 | 0.3133 | 0.67283 | 0.58729 | 0.4642 | 0.30781 | 0.6658 | 0.5786 | 0.45852 | 0.3043 | 0.65281 | 0.56002 | 0.53808 | 0.42772 | 0.31846 | 0.64509 | 0.5523 | 0.52069 | 0.4127 | 0.31429 | 0.68861 | 0.60534 | 0.64547 | 0.6139 | 0.5622 | 0.69309 | 0.68586 | 0.67845 | 0.67142 | 0.65667 | 0.64893 | 0.69349 | 0.60951 | 0.6493 | 0.61754 | 0.56533 | 0.68892 | 0.68209 | 0.67512 | 0.66813 | 0.65352 | 0.6458 | 0.68932 | 0.60534 | 0.64617 | 0.6146 | 0.5622 | 0.68482 | 0.67819 | 0.67128 | 0.66423 | 0.64941 | 0.6417 | 0.68522 | 0.60534 | 0.6421 | 0.6105 | 0.5622
GHG (Mass Basis) | lb/hr |  | 396007.6611 | 340006.6326 | 272005.2973 | 231004.4917 | 391007.582 | 339006.6028 | 267005.2091 | 177003.44 | 387007.5064 | 336006.5402 | 264005.1361 | 174003.3794 | 383007.4283 | 331006.4434 | 260005.0716 | 172003.3398 | 375007.2573 | 320006.2361 | 308005.9917 | 243004.7321 | 180003.5021 | 371007.1787 | 316006.1503 | 298005.7979 | 236004.5929 | 180003.496 | 396007.6654 | 346006.742 | 371007.1829 | 353006.831 | 321006.2594 | 408007.6196 | 352006.5955 | 281005.2678 | 238004.468 | 403007.5265 | 350006.5652 | 276005.1795 | 183003.4218 | 399007.4452 | 346006.4968 | 272005.1043 | 179003.3597 | 395007.3674 | 341006.4008 | 269005.0403 | 177003.3204 | 387007.219 | 330006.1949 | 317005.9521 | 251004.7025 | 186003.4812 | 383007.1339 | 326006.1098 | 307005.7598 | 243004.564 | 185003.4749 | 409007.624 | 358006.7041 | 383007.138 | 364006.7885 | 332006.2182 | 417007.5704 | 359006.5497 | 288005.2627 | 245004.4779 | 412007.4773 | 357006.5237 | 284005.1797 | 189003.4463 | 407007.4011 | 354006.4602 | 280005.1063 | 186003.3859 | 403007.3237 | 348006.3646 | 276005.0437 | 183003.3473 | 395007.1809 | 337006.1602 | 324005.9189 | 258004.7049 | 192003.503 | 391007.096 | 333006.0753 | 314005.7276 | 249004.5398 | 189003.4572 | 417007.5747 | 365006.6588 | 391007.1002 | 372006.7529 | 339006.1842 | 407007.624 | 402007.5444 | 398007.4629 | 394007.3856 | 385007.2233 | 381007.1382 | 407007.6283 | 357006.7046 | 381007.1424 | 362006.7929 | 331006.2186 | 414007.5781 | 410007.503 | 405007.4263 | 401007.3495 | 392007.1887 | 388007.1038 | 414007.5825 | 364006.6588 | 388007.1079 | 369006.7606 | 338006.1842 | 417007.533 | 413007.46 | 409007.3841 | 405007.3065 | 396007.1436 | 391007.0587 | 417007.5374 | 365006.6588 | 391007.0631 | 372006.7155 | 339006.1842
GHG (CO2e Basis) | lb/hr |  | 396381.6609 | 340330.424 | 272263.9043 | 231223.7702 | 391377.7224 | 339328.938 | 267259.5067 | 177171.3735 | 387373.953 | 336325.8211 | 264255.8702 | 174168.3532 | 383370.0628 | 331321.0006 | 260252.6566 | 172166.3839 | 375361.5455 | 320310.6711 | 308298.4931 | 243235.7428 | 180174.4663 | 371357.6312 | 316306.3943 | 298288.8401 | 236228.8081 | 180174.1643 | 396381.8784 | 346335.8727 | 371357.8365 | 353340.3066 | 321311.8309 | 408379.595 | 352328.5756 | 281262.4304 | 238222.5862 | 403374.9558 | 350327.0654 | 276258.0328 | 183170.4674 | 399370.9085 | 346323.6585 | 272254.2876 | 179167.3746 | 395367.0304 | 341318.8743 | 269251.0981 | 177165.4174 | 387359.6367 | 330308.6173 | 317296.5239 | 251234.2688 | 186173.4273 | 383355.3961 | 326304.3767 | 307286.9434 | 243227.3704 | 185173.1132 | 409379.8125 | 358333.988 | 383355.6015 | 364338.1923 | 332309.7771 | 417377.1425 | 359326.2922 | 288262.1767 | 245223.0815 | 412372.5033 | 357324.9995 | 284258.0449 | 189171.6876 | 407368.7097 | 354321.8342 | 280254.3842 | 186168.6794 | 403364.8558 | 348317.0742 | 276251.2672 | 183166.7584 | 395357.7399 | 337306.8896 | 324294.8687 | 258234.3896 | 192174.5146 | 391353.5114 | 333302.6612 | 314285.3366 | 249226.1623 | 189172.2313 | 417377.36 | 365331.7288 | 391353.7168 | 372336.4164 | 339308.0857 | 407379.8125 | 402375.8498 | 398371.7905 | 394367.9365 | 385359.8541 | 381355.6136 | 407380.0299 | 357334.0122 | 381355.819 | 362338.4098 | 331309.8012 | 414377.5291 | 410373.7839 | 405369.9662 | 401366.1364 | 392358.1265 | 388353.898 | 414377.7466 | 364331.7288 | 388354.1034 | 369336.803 | 338308.0857 | 417375.282 | 413371.6455 | 409367.864 | 405363.998 | 396355.8794 | 391351.6509 | 417375.4994 | 365331.7288 | 391351.8684 | 372334.5558 | 339308.0857
NOx | lb/MMBtu |  | 0.0073122 | 0.0072761 | 0.0072789 | 0.0072886 | 0.0073245 | 0.0072722 | 0.0072626 | 0.0072612 | 0.0073337 | 0.0072676 | 0.0072714 | 0.0072479 | 0.0073129 | 0.0072638 | 0.0072682 | 0.0072611 | 0.0073181 | 0.007272 | 0.0072854 | 0.0072772 | 0.007271 | 0.0073306 | 0.0072552 | 0.0072779 | 0.0072866 | 0.0072836 | 0.0073397 | 0.0072659 | 0.0073264 | 0.0073488 | 0.0072837 | 0.007352 | 0.007317 | 0.0073198 | 0.0073274 | 0.0073463 | 0.0073138 | 0.0073041 | 0.0072998 | 0.0073613 | 0.0073162 | 0.0073166 | 0.0072903 | 0.0073733 | 0.0073123 | 0.0073133 | 0.0073035 | 0.0073569 | 0.0073204 | 0.007293 | 0.007323 | 0.0073145 | 0.0073767 | 0.0073033 | 0.007326 | 0.0072795 | 0.0073278 | 0.0073478 | 0.0073069 | 0.0073724 | 0.007359 | 0.007332 | 0.0073678 | 0.0073312 | 0.0073269 | 0.0073111 | 0.0073622 | 0.0073231 | 0.0073037 | 0.0073183 | 0.0073725 | 0.0073201 | 0.0073138 | 0.0073055 | 0.0073841 | 0.0073157 | 0.0073084 | 0.0073172 | 0.0073959 | 0.0073223 | 0.007334 | 0.0073192 | 0.0073382 | 0.0073818 | 0.0073048 | 0.0073249 | 0.0073184 | 0.0072952 | 0.0073635 | 0.0073203 | 0.0073776 | 0.0073978 | 0.007333 | 0.0073478 | 0.007361 | 0.0073439 | 0.0073551 | 0.0073524 | 0.0073722 | 0.0073436 | 0.0073064 | 0.0073679 | 0.0073543 | 0.0073314 | 0.0073602 | 0.0073693 | 0.0073801 | 0.0073583 | 0.0073879 | 0.0073738 | 0.007356 | 0.0073203 | 0.0073695 | 0.0073893 | 0.007333 | 0.0073721 | 0.0073792 | 0.0073894 | 0.0073683 | 0.0074006 | 0.0073865 | 0.0073678 | 0.0073203 | 0.007382 | 0.0074029 | 0.007333
SO2 | lb/MMBtu |  | 0.0012662 | 0.0012797 | 0.0012818 | 0.0012958 | 0.0012794 | 0.0012855 | 0.001257 | 0.0012689 | 0.0012923 | 0.0012607 | 0.0012748 | 0.0012917 | 0.0012732 | 0.0012796 | 0.0012911 | 0.0012344 | 0.0012698 | 0.0012833 | 0.0012547 | 0.0012812 | 0.0012465 | 0.0012837 | 0.0012618 | 0.0012548 | 0.0012672 | 0.0012486 | 0.0012655 | 0.0012589 | 0.001283 | 0.001278 | 0.0012785 | 0.0011139 | 0.0011031 | 0.0011049 | 0.0010855 | 0.0011277 | 0.0011082 | 0.0011237 | 0.0011339 | 0.0011075 | 0.0011198 | 0.0010927 | 0.0010827 | 0.0011192 | 0.0010987 | 0.0011066 | 0.0010955 | 0.0011086 | 0.0010961 | 0.0011001 | 0.0011345 | 0.0011146 | 0.0011218 | 0.0011114 | 0.0010947 | 0.0011158 | 0.0011166 | 0.0011133 | 0.0011214 | 0.0011212 | 0.0011074 | 0.001131 | 0.00099305 | 0.00096268 | 0.0009677 | 0.00097482 | 0.00097298 | 0.00096651 | 0.00098319 | 0.00098515 | 0.00098299 | 0.00097601 | 0.00099734 | 0.0010027 | 0.00099338 | 0.00099066 | 0.00096163 | 0.0010143 | 0.00097937 | 0.00098417 | 0.00098332 | 0.00097933 | 0.00096919 | 0.00099108 | 0.00099792 | 0.00097383 | 0.00096154 | 0.00098204 | 0.00099248 | 0.00098332 | 0.0009905 | 0.0010055 | 0.00098035 | 0.0011451 | 0.001125 | 0.0011373 | 0.0011492 | 0.0011415 | 0.0011551 | 0.0011445 | 0.0011213 | 0.0011544 | 0.0011424 | 0.0011309 | 0.001024 | 0.0010343 | 0.0010123 | 0.0010229 | 0.0010458 | 0.0010241 | 0.0010234 | 0.00098332 | 0.0010235 | 0.0010402 | 0.00098035 | 0.00096578 | 0.00097523 | 0.00095241 | 0.00096253 | 0.00095054 | 0.00096197 | 0.00096522 | 0.00098332 | 0.00096137 | 0.0009389 | 0.00098035
Total Particulates | lb/MMBtu |  | 0.0044633 | 0.0034698 | 0.0041522 | 0.0047619 | 0.0044139 | 0.0034818 | 0.0042086 | 0.0059852 | 0.0044584 | 0.0035077 | 0.0042589 | 0.0060782 | 0.0045052 | 0.0035491 | 0.0043035 | 0.0061356 | 0.0046448 | 0.0036438 | 0.0037601 | 0.0045559 | 0.0058929 | 0.0046956 | 0.0036828 | 0.0038606 | 0.0046729 | 0.0058962 | 0.0044608 | 0.0049639 | 0.0046929 | 0.0048992 | 0.0052691 | 0.0050286 | 0.0041549 | 0.005064 | 0.0058076 | 0.0050264 | 0.0041741 | 0.0051035 | 0.0073707 | 0.0050487 | 0.004218 | 0.0051786 | 0.0075069 | 0.005102 | 0.0042813 | 0.0052444 | 0.0075957 | 0.0052741 | 0.0043844 | 0.0045225 | 0.0055696 | 0.0073145 | 0.0053371 | 0.0044455 | 0.0046735 | 0.0057386 | 0.0073278 | 0.0050258 | 0.005643 | 0.005334 | 0.0055728 | 0.006006 | 0.0053817 | 0.0045542 | 0.0055297 | 0.0063905 | 0.0053514 | 0.0045723 | 0.0056182 | 0.0081627 | 0.0053737 | 0.0046173 | 0.0056991 | 0.0083083 | 0.0054636 | 0.0046866 | 0.0057698 | 0.008404 | 0.0056398 | 0.0048421 | 0.0049986 | 0.0061337 | 0.0080305 | 0.0057073 | 0.0048699 | 0.0051232 | 0.0063568 | 0.0081369 | 0.0053786 | 0.0060456 | 0.0057039 | 0.0059614 | 0.0064703 | 0.0050576 | 0.0050466 | 0.0050692 | 0.0051551 | 0.0053045 | 0.0053678 | 0.0050547 | 0.0056426 | 0.0053647 | 0.0056049 | 0.0060445 | 0.0054082 | 0.0053977 | 0.0054208 | 0.0055105 | 0.0056674 | 0.0057352 | 0.0054051 | 0.0060456 | 0.0057318 | 0.0059904 | 0.0064703 | 0.005344 | 0.0053313 | 0.0053532 | 0.0054433 | 0.0056014 | 0.0056687 | 0.0053409 | 0.0060456 | 0.0056652 | 0.0059223 | 0.0064703
Sulfur Mist | lb/MMBtu |  | 0.00082302 | 0.00080439 | 0.00082402 | 0.00080985 | 0.0008316 | 0.00080802 | 0.00083799 | 0.00084596 | 0.00080768 | 0.00081575 | 0.00080268 | 0.00078938 | 0.00081617 | 0.000828 | 0.00081289 | 0.00079872 | 0.00083539 | 0.00081664 | 0.00080949 | 0.00081997 | 0.00083097 | 0.00081076 | 0.00082804 | 0.00083654 | 0.00079202 | 0.00083241 | 0.00082255 | 0.00082731 | 0.00081029 | 0.00081653 | 0.00081361 | 0.00073202 | 0.00069861 | 0.00073658 | 0.0007056 | 0.00070885 | 0.00070183 | 0.00070231 | 0.00070872 | 0.00071659 | 0.00070922 | 0.00071266 | 0.00072181 | 0.00072416 | 0.00071986 | 0.00072171 | 0.00073035 | 0.00070546 | 0.00070464 | 0.00073338 | 0.00072198 | 0.00069662 | 0.00071387 | 0.00071446 | 0.00071576 | 0.00069075 | 0.00069789 | 0.0007316 | 0.00072346 | 0.00071346 | 0.00071446 | 0.000702 | 0.00064068 | 0.00062944 | 0.00064513 | 0.00064988 | 0.00064866 | 0.00063195 | 0.00060864 | 0.00063331 | 0.00062256 | 0.00063816 | 0.0006174 | 0.00064461 | 0.00062914 | 0.00064774 | 0.00062506 | 0.00065203 | 0.00064165 | 0.00062987 | 0.00061458 | 0.00061852 | 0.00062305 | 0.00064933 | 0.00063867 | 0.00063511 | 0.00064103 | 0.00063131 | 0.00064031 | 0.00061913 | 0.00064895 | 0.00064641 | 0.00062743 | 0.0007316 | 0.00073931 | 0.00074738 | 0.00072238 | 0.0007386 | 0.00074741 | 0.00073118 | 0.00072341 | 0.00074698 | 0.00074971 | 0.00070195 | 0.00067202 | 0.00064643 | 0.0006531 | 0.00065994 | 0.0006747 | 0.00064862 | 0.00067163 | 0.00061913 | 0.00064824 | 0.00068154 | 0.00062743 | 0.00061166 | 0.00061765 | 0.00062399 | 0.00063062 | 0.00061106 | 0.00061841 | 0.00061131 | 0.00061913 | 0.00061803 | 0.0006139 | 0.00062743
The notes page is an integral part of this document and must be reviewed prior to use of this data.
Worst Case Operating Parameters |  | Overall | 1: NG Only; 2: Wet Gas; 3: Ethane 50%; 4: Wet Gas/NG; 5: 50%C2/NG; 6: 50%C2/100%C2
GT Heat Consumption per unit with Permitting Margin See HRSG NOTE 10 | MMBTU/hr, HHV | 2737.7 | 1: 2737.7; 2: 2722.3; 3: 2703.4; 4: 2722.3; 5: 2703.4; 6: 2703.4
Duct Burner Heat Consumption | MMBTU/hr, HHV | 424.1 | 1: 424.1; 2: 422.3; 3: 420.9; 4: 424.1; 5: 424.1; 6: 405.5
Worst Case Emission Rates - MAX |  | Overall | 1: NG Only; 2: Wet Gas; 3: Ethane 50%; 4: Wet Gas/NG; 5: 50%C2/NG; 6: 50%C2/NG
NOx | lb/hr | 23.2 | 1: 23.2; 2: 23.1; 3: 23; 4: 23.1; 5: 23; 6: 22.9
CO | lb/hr | 14.1 | 1: 14.1; 2: 14.1; 3: 14; 4: 14.1; 5: 14; 6: 14
VOC | lb/hr | 8.1 | 1: 8.1; 2: 8.1; 3: 8; 4: 8.1; 5: 8; 6: 8
SO2 (with margin, NG/WG/Ethane corrected to 0.4 gr/100scf sulfur content) | lb/hr | 4 | 1: 4; 2: 3.5; 3: 3.1; 4: 3.6; 5: 3.2; 6: 3
PM/PM10/PM2.5 | lb/hr | 16.9 | 1: 14.1; 2: 15.8; 3: 16.8; 4: 15.9; 5: 16.9; 6: 16.6
H2SO4 (with margin, NG/WG/Ethane corrected to 0.4 gr/100scf sulfur content) | lb/hr | 2.6 | 1: 2.6; 2: 2.3; 3: 2; 4: 2.3; 5: 2.1; 6: 1.9
CO2 | lb/hr | 417000 | 1: 396000; 2: 409000; 3: 417000; 4: 407000; 5: 414000; 6: 417000
CH4 | lb/hr | 6.9686 | 1: 6.9686; 2: 6.9309; 3: 6.8861; 4: 6.9349; 5: 6.8932; 6: 6.8522
N2O | lb/hr | 0.69686 | 1: 0.69686; 2: 0.69309; 3: 0.68861; 4: 0.69349; 5: 0.68932; 6: 0.68522
GHG (Mass Basis) | lb/hr | 417007.5747 | 1: 396007.6654; 2: 409007.624; 3: 417007.5747; 4: 407007.6283; 5: 414007.5825; 6: 417007.5374
GHG (CO2e Basis) | lb/hr | 417377.36 | 1: 396381.8784; 2: 409379.8125; 3: 417377.36; 4: 407380.0299; 5: 414377.7466; 6: 417375.4994
NOx | lb/MMBtu | 0.0074006 | 1: 0.0073488; 2: 0.0073767; 3: 0.0073978; 4: 0.0073722; 5: 0.0073893; 6: 0.0074006
SO2 (with margin, NG/WG/Ethane @ 0.4 gr/100scf sulfur content) | lb/MMBtu | 0.0012958 | 1: 0.0012958; 2: 0.0011345; 3: 0.0010143; 4: 0.0011551; 5: 0.0010458; 6: 0.00098332
PM/PM10/PM2.5 | lb/MMBtu | 0.008404 | 1: 0.0061356; 2: 0.0075957; 3: 0.008404; 4: 0.0060445; 5: 0.0064703; 6: 0.0060456
H2SO4 (with margin, NG/WG/Ethane @ 0.4 gr/100scf sulfur content) | lb/MMBtu | 0.00084596 | 1: 0.00084596; 2: 0.00073658; 3: 0.00065203; 4: 0.00074971; 5: 0.00068154; 6: 0.00063062
Gas Turbine fuel LHV |  |  | 1: 21089; 2: 20786; 3: 20694; 4: 20786; 5: 20694; 6: 20694
Gas Turbine fuel HHV (Btu/lb) |  |  | 1: 23340; 2: 22909; 3: 22728; 4: 22909; 5: 22728; 6: 22728
The potential short-term emission rates for NOx, CO, SO2, PM, PM10, PM2.5, VOC, H2SO4, and CO2 for the CTs/DBs are established by selecting the maximum lb/hr emission rates across the expected fuel types, operating loads, and ambient temperature ranges.
Grains/pound | 7000
T218 Fuel Sulfur Content (gr/100 scf) | 0.5
Proposed Fuel Sulfur Content (gr/100 scf) | 0.4
T218 Natural Gas Fuel Sulfur Content (ppm) | 12.4
T218 Wet Gas Fuel Sulfur Content (ppm) | 10.6
T218 Ethane Blend Fuel Sulfur Content (ppm) | 9.3
Molecular weight of SO2 | 64
Molecular weight of S | 32
Conversion Factor (kg to lb) | 2.2046
CO2 Emission Factor (kg/MMBtu) | 53.06
CO2 Emission Factor (lb/MMBtu) | 116.9771
CH4 Emission Factor (kg/MMBtu) | 0.001
CH4 Emission Factor (lb/MMBtu) | 0.0022046
N2O Emission Factor (kg/MMBtu) | 0.0001
N2O Emission Factor (lb/MMBtu) | 0.00022046
Global Warming Potential - CO2 | 1
Global Warming Potential - CH4 | 25
Global Warming Potential - N2O | 298

## RevI_Cover
SIZE | DWG NO | SH | REV | REVISIONS
A | 100A6302 | 1 | I
THIS DOCUMENT SHALL BE REVISED IN ITS ENTIRETY ALL SHEETS OF THIS DOCUMENT ARE THE SAME REVISION LEVEL AS INDICATED IN THE REVISION BLOCK |  |  |  | REV | DESCRIPTION |  |  | DATE (dd-mmm-yyyy) | APPROVED
|  |  |  | - | Preliminary Issue |  |  | 2015-08-06 | C. Matis
|  |  |  | A | Preliminary Issue |  |  | 2015-09-25 | H. Xu
|  |  |  | B | Preliminary Issue |  |  | 2015-01-12 | H. Xu
|  |  |  | C | Preliminary Issue |  |  | 2016-09-09 | H. Xu
|  |  |  | D | For Use in Design |  |  | 2016-09-26 | H. Xu
|  |  |  | E | For Use in Design |  |  | 2016-10-07 | L. Camire
|  |  |  | F | For Use in Design |  |  | 2017-01-26 | C. Matis
|  |  |  | G | For Use in Design |  |  | 2017-03-24 | H. Xu
|  |  |  | H | For Use in Design |  |  | 2017-04-17 | H. Xu
|  |  |  | I | For Use in Design |  |  | 2017-04-24 | H. Xu
Combined Cycle Systems
Combined Cycle Systems Emissions Estimates
2x1 7HA.01 MS
© COPYRIGHT 2015 General Electric - Proprietary Information
All Rights Reserved. This document contains proprietary information. No part of this document may be used by or disclosed to others, reproduced, transmitted, stored in a retrieval system nor translated into any human or computer language, in any form or any means, electronic, mechanical magnetic, optical, chemical, manual or otherwise, without the prior written permission of the General Electric Company.
SIGNATURES |  |  | DATE (dd-mmm-yyyy) |  | g GE Power |  |  | GENERAL ELECTRIC COMPANY GENERAL ELECTRIC INTERNATIONAL, INC. POWER PLANT SYSTEMS
PREPARED BY |  |  | 2015-08-06
Tonya Watkins
SYSTEM ENGINEER |  |  | 2015-08-06
Rich Vanderwood
PROJECT ENGINEER |  |  | 2015-08-06 |  | ESC Brooke County
Gary Chmiel
ISSUED |  |  | 2015-08-06
Han Xu |  |  |  |  | MADE FOR: IPS # 1023669 |  |  | MDL - T218
FIRST MADE FOR: |  |  |  |  | SIZE A | CAGE CODE | NONE | DWG NO | 100A6302
ESC Brooke County |  |  |  |  | SCALE | NONE |  | SHEET | 1 of 7
DT-7N |  |  | Class I GE Information |  |  |  | Copyright 2015, General Electric Company and its Affiliates

## RevI_Revisions
Drawing Revision Status
Revision | Date | Description
- | 2015-08-06 | Initial issue
A | 2015-09-25 | Updated VOC and PM stack numbers
B | 2015-01-12 | Revised 7HA.01 GT cycle deck performance and revised CCHB modeling for Ethane-ST doping
C | 2016-09-09 | Configuration change due to new site along with Duct Firing: elevation change with ACC; micromixer DLN in lieu of steam doping; Revised 7HA.01 GT cycle deck performance
D | 2016-09-26 | Natural Gas only based on DLN 2.6+ combustor
E | 2016-10-07 | Added duct firing cases. Based on DLN 2.6+ combustor.
F | 2017-01-26 | Updated GT Cycle Deck, updates to NG, Blended fuel, and Wet gas cases. Based on micromixer DLN combustor.
G | 2017-03-24 | Updated sulfur to 0.4gr/100SCF for all fuel types. Based on micromixer DLN combustor.
H | 2017-04-17 | Based on DLN 2.6+ combustor. Updated fuel sulfur content to 0.4gr/100SCF. (Rev E with Sulfur content updated to 0.4 gr/100SCF)
I | 2017-04-24 | Based on micromixer DLN combustor. Added 100% ethane duct firing cases. (Rev G with added cases for 50% ethane in GT and 100% ethane in DB, all fules at 0.4 gr/100SCF)

## RevI_CustNotes
Estimated Steady State Emission Notes
HRSG Emission Notes:
1 | Gas turbine(s) and steam plant are in steady-state operation.
2 | Steady State Emissions data above are estimated values based on GE recommended measurements and analysis procedures, per GEK 28172.
3 | SO2 emission values have been estimated by assuming that all the sulfur in the fuel is converted to SO2.
4 | SO2 and sulfur mist emission values are based on maximum sulfur content of: Fuel Fuel Molecular Weight Gr/100SCF ppmw NG 17.54 0.4 12.4 Wet Gas 20.42 0.4 10.6 50% Ethane 23.34 0.4 9.3 100% Ethane 30.07 0.4 7.2
5 | SO2 and sulfur mist values are margined by 20% to account for variation in fuel sulfur content and measurement error.
6 | The CO2 estimates are margined 5% to account for equipment variation and site operating conditions. If CO2 compliance is to be demonstrated using actual CO2 measurement from the HRSG stack, GE recommends an additional 10% margin to the estimated values.
7 | Sulfur mist emission calculations conservatively assume that all SO3 combines with water to form sulfur mist. In actuality, some SO3 may form other chemical species. This would include ammonium sulfates in the presence of NH3. The maximum sulfur mist is reported to be conservative.
8 | The estimated values for heat consumption and exhaust flows are margined in this document to account for equipment variations, site operating conditions, and life-cycle operating parameters.The Plant Performance section does not include permitting margin, for more information on performance please refer to the Heat Balance.
Additional Notes for Particulate Emissions
1 | Particulate Matter estimates over the entire emissions compliance region of GT operation are based on field data obtained at base load for the GT. In reality, particulate matter emissions measured in lb/h are expected to decrease at part load operation and the lb/MMBTU values at part load operation are expected not to exceed the lb/MMBTU value for PM at baseload.
2 | PM10 and PM2.5 are estimated at the same rate as Total Particulates.
3 | PM estimates are based on maximum S content in the fuel of: Fuel Fuel Molecular Weight Gr/100SCF ppmw NG 17.54 0.4 12.4 Wet Gas 20.42 0.4 10.6 50% Ethane 23.34 0.4 9.3 100% Ethane 30.07 0.4 7.2